REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

ECD

# LIMBE III COUNCIL INTERNAL TENDERS BOARD

# OPEN NATIONAL INVITATION TO TENDER

# (BY EMERGENCY PROCEDURE)

THE PROJECT OWNER

THE MAYOR OF LIMBE III COUNCIL

TENDER BOARD

LIMBE III COUNCIL INTERNAL TENDERS BOARD

TENDER FILE No. 009/ONIT/LIIIC/L3C.TB/2026 OF 04/03/2026 FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

FINANCING: PUBLIC INVESTMENT BUDGET

FINANCIAL YEAR 2026

MARCH 2026

TABLE OF CONTENTS

LIMBE III COUNCIL INTERNAL TENDERS BOARD	1

OPEN NATIONAL INVITATION TO TENDER	1

(BY EMERGENCY PROCEDURE)	1

DOCUMENT No. 1 – TENDER NOTICE	3

OPEN NATIONAL INVITATION TO TENDER	4

(BY EMERGENCY PROCEDURE)	4

TENDER FILE	11

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY	30

34

II. SPECIFIC ENVIRONMENTAL AND SOCIAL CLAUSES	54

1	Information and accompanying measures	54

2	Site installations	55

3	Treatment and waste management	55

4	Preventive measures against noise pollution and dust emissions	56

5	Storage and use of potentially polluting substances	56

6	Fuels and lubricants	56

7	Other potentially polluting substances	56

8	Management of accidental pollution	56

9	Response to accidental pollution	56

10	Protection of natural areas against fire	56

11	Preserving the landscape integrity of the site	57

12	Social and cultural aspects	57

13	Safety of people and property	57

14	Abandonment of installations at the end of the works	57

BILL OF QUANTITIES AND ESTIMATES	60

TENDER FILE	63

TENDER FILE	72

TENDER FILE	74

# DOCUMENT No. 1 – TENDER NOTICE

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

TENDER NOTICE

# OPEN NATIONAL INVITATION TO TENDER

# (BY EMERGENCY PROCEDURE)

No. 009/ONIT/LIIIC/L3C.TB/2026 OF 02/04/2026 FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

FINANCING: PUBLIC INVESTMENT BUDGET, FINANCIAL YEAR 2026

- Subject of the invitation to tender:

The Mayor of LIMBE III Council, the Contracting Authority, hereby launches an Open National Invitation to Tender FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY.

- Nature of services

The works comprise the outcome of the preliminary studies carried out and the detailed information provided in the technical specifications. (Document V)

- Execution deadline

The maximum duration provided by the Project Owner for the execution of the works forming the subject of this invitation to tender is Three (03) months. This period runs from the date of notification of the service order to start the work.

- Number of Lots

Not applicable

- Estimated cost

The estimated cost after preliminary studies stands at CFA Francs Sixteen million five hundred thousand (16,500,000) francs CFA including taxes.

- Participation and origin

The tender is open to duly registered Cameroonian enterprises that fulfill the requirements of the invitation to tender.

- Financing

Rehabilitation which form the subject of this invitation to tender shall be financed by PUBLIC INVESTMENT BUDGET 2026 financial year, budget head 60323423320000030630523412

- Bid bond

Each bidder must include in his administrative documents, a bid bond issued by a first-rate banking establishment approved by the Ministry in charge of finance and whose list is found in document No. 14 of the Tender File, of an amount of three hundred and thirty thousand (330,000) francs CFA and valid for thirty (30) days beyond the initial date limit of validity of bids.

The bid bond provide in accordance with the Circular Letter No. 000019/LC/MINMAP of 5th of June 2024 relating to the modalities of constitution, deposit, conservation, restitution and withdrawal of bond on public contracts.

The absence of the bid bond issued by Thirty thousand (30,000) CFA francs, a first-rate bank or financial body of first category authorized by the Minister in charge of Finance to issue bonds for public contracts shall lead to the immediate rejection of the offer. A bid bond submitted but that does not have any relation with the consultation concerned shall be considered as absent. The bid bond presented by a tenderer at the bid opening session shall not be accepted.

- Consultation of tender file

The file may be consulted online on the COLEPS platform

- Acquisition of tender file

The file may be obtained from COLEPS platform as soon as this notice is published against payment of the sum of Thirty thousands (30.000) FCFA payable at Limbe III Municipal Treasury

- Submission of bids

For online submission by electronic means, the offer must be transmitted by the bidder on the COLEPS platform. A backup copy of the offer saved on a USB key or CD/DVD must be sent in a sealed envelope with the clear and legible indication "backup copy", in addition to the above mention latest 02/04/2026 at 12 noon.

N.B.: File size and format. The maximum sizes of the documents that will transit on the platform and constitute the bidder's offer are as follows:

• 5 MB for the Administrative file;

- 15 MB for the Technical file

• 5 MB for the Financial Offer

The accepted formats are as follows:

• PDF format for text documents;

JPEG for images

The candidate will ensure that compression software is used to possibly reduce the size of the files to be transmitted in accordance with the sizes indicated above.

OPEN NATIONAL INVITATION TO TENDER No. 009/ONIT/LIIIC/L3C.TB/2026 OF 04/03/2026

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

(EMERGENCY PROCEDURE)

###### ‘To be opened only during the bid-opening session’’

In case of any ambiguities or differences, only the original shall be considered authentic.

- Acceptability of bids

Any bid that does not respect the mode of separation of the financial, administrative and technical bids shall be rejected.

Any bid not in compliance with the prescriptions of the Tender File shall be declared inadmissible. This refers especially to the absence of a bid bond issued by CDEC and a first-rate bank approved by the Minister in charge of Finance. Notably, the absence of bid bond delivered by a first order bank approved by the Minister in charge of Finance valid for thirty (30 days after the validity of bids.

Under penalty of being rejected, only originals or true copies certified by the issuing service or administrative authorities and must imperatively be produced in accordance with the Special Regulations of the invitation to tender. They must obligatorily be not older than three (3) months before the latest date set for the opening of bids. Cumulative bidding shall not be accepted.

- Opening of bids

The bids shall be opened in a single phase on the 02/04/2026 at 1PM local time by the Limbe III Internal Tenders Board in the Conference Hall of the Limbe III Council situated at Chop Farm - Bimbia. Only tenderers may attend this opening session or be represented by a single person of their choice, duly authorized, even in the case of a group of companies. Under pain of being rejected, the required administrative documents must be submitted in originals or copies certified by the issuing service or the relevant administrative authority, in accordance with the provisions of the Special Regulations of the invitation to tender. They shall be no later than Three (3) months old from the original deadline for the submission of tenders or must have been issued after the date of signature of the Tender Notice. In case of absence or non-conformity of a document in the administrative file during the opening of bids, after a 48 (forty-eight) hours deadline granted by the Board, the file shall be rejected.

NB: The original copies of the Administrative documents must be presented for verification during the opening of bids session

- Evaluation criteria

The evaluation of bids shall be carried out in three stages:

  - 1st Stage: verification of the presence and conformity of each administrative document;

  - 2nd Stage: Analysis of technical offer

  - 3rd Analyses of the financial bids.

The criteria of evaluation shall be as follows.

- Eliminatory criteria

The eliminatory criteria are the following:

- Absence of bid bond at the opening of bids with its consignment receipt delivered by the CDEC;

- Absence of categorization certificate issued by the Authority in charge of Public Contracts

- Failure to submit, beyond the 48 (forty-eight) hours deadline after the opening of bids, a document of the administrative file deemed non-compliant or absent (except the bid bond);

- False declarations, fraudulent schemes or forged documents;

- Failure to comply with 70% essential criteria (70% referring to the qualification threshold of technical bids);

- Absence of the sworn statement for not having abandoned contracts during the last three years;

- Failure to comply with bids file format;

- Absence of a quantified unit price in the financial offer;

- Absence of own or hired minimum equipment;

- Absence of the site engineer;

- Absence of an element in the financial offer (submission, Bill of quantities and cost estimate, Schedule of Unit Prices, Sub-detail of Unit Price);

- Absence of the integrity charter dated and signed;

Absence of the dated and signed commitment statement to comply with environmental and social clauses.

  - Main qualification criteria

The criteria relating to the qualification of candidates are the following:

- Financial situation

- Experience

- Personnel

- Equipment

- Technical proposal (methodology and planning of execution)

N.B.: Non-respect of least at 70% of essential criteria shall entail rejection of the bid.

- Award

The contract shall be awarded to lowest bidder fulfilling the best technical and financial conditions

- Validity of bids

Bidders will remain committed to their bids for ninety (90) days from the initial deadline set for the submission of bids.

- Complementary information

Complementary information may be obtained during working hours from Limbe III Council, Service for award of contracts (CDO’s office), Tel: 677629600, Email: limbe3councilbimbia@yahoo.com

LIMBE III, the 04/03/2026

THE LORD MAYOR OF LIMBE III COUNCIL

The Project Owner

Copies:

- SDO/FAKO

- MINMAP/DD-FAKO,

- ARMP/SW,

- Chairpersons of TB,

- Notice Boards.

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

AVIS D’APPEL D’OFFRES NATIONAL OUVERT

(EN PROCEDURE D’URGENCE)

N°009/AONO/C.LIII/CIPM/PIB2026 DU 04/03/2026 POUR LA RÉHABILITATION DE TROIS FORAGES ET D'UN BASSIN VERSANT AVEC CONDUITE DE DISTRIBUTION À BONANGOMBE, BONABILE, CHOP FARM, BAIE DE MAN O' WAR

Financement : Budget d’Investissement Publique, Exercice 2026

- Objet de l'Appel d'Offres

Le Maire de la Commune de Limbe III, l’Autorité Contractante lance un Appel d’Offres National Ouvert en procédure d’urgence POUR LA RÉHABILITATION DE TROIS FORAGES ET D'UN BASSIN VERSANT AVEC CONDUITE DE DISTRIBUTION À BONANGOMBE, BONABILE, CHOP FARM,  MAN O' WAR BAY

###### Consistance des travaux

Les travaux comprennent notamment la production des études préliminaire fait sur le site, les informations détailler fournit dans les spécifications technique et dans les devis quantitatif par rapport aux dessins et spécifications prévus. (Document V)

- Délais d’exécution

Le délai maximum  prévu par le Maître d’Ouvrage ou le Maître d’Ouvrage Délégué pour la réalisation des travaux objet du présent appel d’offres est de Trois (03) mois. Ce délai court à compter de la date de notification de l’ordre de servie de commencer les travaux.

- Allotissement

Les travaux sont en un lot unique

- Coût prévisionnel

Le coût prévisionnel des travaux après les études préliminaires est de Seize millions cinq cents milles (16,500,000) francs CFA Toutes Taxes Comprises.

- Participation et origine

Sont éligibles les entrepreneurs Camerounais ayant l’expérience et les capacités techniques et financières requises dans le Dossier d'Appel D'offres

- Financement

Les  travaux objet  du  présent  appel  d'offres sont financés par le budget d’investissement publique, Exercice 2026, Imputation : 60323423320000030630523412

- Cautionnement provisoire

Chaque soumissionnaire doit joindre à ses pièces administratives, un cautionnement de soumission établie par une banque de premier ordre agréée par le Ministère chargé des finances et dont la liste figure dans la pièce 14 du DAO, précisant un montant de trois cent trente milles (330,000) francs CFA et valable pendant trente (30) jours au-delà de la date initiale de validité des offres.

Le cautionnement de soumission devra être établi et fourni conformément à la Lettre-circulaire N°000019/LC/MINMAP du 05 juin 2024 relative aux modalités de constitution, de consignation, de conservation, de restitution et de déconsignation des cautionnements sur les marchés publics.

Le cautionnement provisoire sera libéré d'office au plus tard quinze (15) jours à compter de la date d’attribution de marches pour les soumissionnaires n'ayant pas été retenus. Dans le cas où le soumissionnaire est attributaire de la lettre commande, le cautionnement provisoire sera libéré après constitution du cautionnement définitif.

L’absence du cautionnement de soumission délivrée par une banque de premier ordre ou un organisme financier de première catégorie autorisé par le Ministère chargé des Finances à émettre des cautions dans le cadre des marchés publics, entraînera le rejet pur et simple de l'offre. Une caution de soumission produite mais n'ayant aucun rapport avec la consultation concernée est considérée comme absente. La caution de soumission présentée par un soumissionnaire au cours de la séance d’ouverture des plis est irrecevable.

###### Consultation du Dossier d'Appel d'Offres

Le dossier peut être consulté en ligne sur la plateforme COLEPS

- Acquisition du Dossier d'Appel d'Offres

Le dossier peut être obtenu sur la plateforme COLEPS dès la publication du présent avis contre paiement d’une somme non remboursable de Trente milles (30,000) francs CFA, payable à la Recette Municipale de la Commune de LIMBE III. Cette quittance devra identifier le payeur comme représentant l’entreprise désireuse de participer à l’Appel d’Offres.

- Remise des offres

Pour la soumission en ligne par voie électronique, l’offre devra être transmise par le soumissionnaire sur la plateforme COLEPS Au plus tard le 02/04/2026 à 12h. Une copie de sauvegarde de l’offre enregistrée sur clé USB devra être transmise sous pli scellé avec l’indication claire et lisible « copie de sauvegarde », en plus de la mention ci-dessus dans les délais impartis.

N.B : Taille et format des fichiers pour la soumission en ligne, les tailles maximales des documents qui vont transiter sur la plateforme et constituant l’offre du soumissionnaire sont les suivantes :

- 5 Mo pour le dossier Administrative;

- 15 Mo pour l’Offre Technique;

- 5 Mo pour l’Offre Financière

Les formats acceptés sont les suivants :

- Format PDF pour les documents textuels ; JPEG pour les images. Le candidat veillera à utiliser des logiciels de compression afin de réduire éventuellement la taille des fichiers à transmettre conformément aux tailles sus-indiquées.

NB: Toute offre incomplète conformément aux prescriptions du Dossier d'Appel d'Offres sera déclarée irrecevable.

Notamment l'absence de la caution de soumission délivrée par un organisme ou une institution financière agréée par le Ministre en charge des finances pour émettre les cautions dans le domaine des marchés publics ou le non-respect des modèles des pièces du Dossier d'Appel d'Offres, entraînera le rejet pur et simple de l'offre sans aucun recours. Une caution de soumission produite mais n'ayant aucun rapport avec la consultation concernée est considérée comme absente. La caution de soumission présentée par un soumissionnaire au cours de la séance d’ouverture des plis est irrecevable devra porter la mention :

- Enveloppe A : pièces administratives;

- Enveloppe B: offre technique.

- Enveloppe C: offre financière.

AVIS D’APPEL D’OFFRES NATIONAL OUVERT

(EN PROCEDURE D’URGENCE)

N°009/AONO/C.LIII/CIPM/PIB2026 DU 04/03/2026 POUR LA RÉHABILITATION DE TROIS FORAGES ET D'UN BASSIN VERSANT AVEC CONDUITE DE DISTRIBUTION À BONANGOMBE, BONABILE, CHOP FARM, MAN O' WAR BAY

« A n’ouvrir qu’en séance de dépouillement »

###### (En Procédure d’urgence)

Les offres parvenues après les dates et heure limites de dépôt des offres ne seront pas reçues.

###### Recevabilité des offres

Chaque soumissionnaire devra joindre à ses pièces administratives, une caution de soumission établi par CDEC et une banque de premier ordre agréée par le Ministère chargé des finances et dont la liste figure dans la pièce 12 du DAO, Elles devront obligatoirement être datées de moins de trois (03) mois précédant la date originale de dépôt des offres ou avoir été établies postérieurement à la date de signature de l’Avis d’Appel d’Offres.

Toute offre incomplète conformément aux prescriptions du Dossier d’Appel d’Offres sera déclarée irrecevable. Notamment l’absence de la caution de soumission délivrée par une banque de premier ordre ou par une compagnie d’assurance agréée par le Ministère chargé des finances.

###### Ouverture des plis

L’ouverture des plis se fera en un temps et aura lieu le 02/04/2026 à 13 heures par la Commission  de  Passation des Marchés de la Commune de Limbe III dans la salle de délibération de l’Hôtel de Ville de la Commune sise à la Commune de LIMBE III. Seuls les soumissionnaires peuvent assister à cette séance d'ouverture ou s'y faire représenter par une personne de leur choix ayant une parfaite connaissance du dossier et mandater à cet effet.

###### Critères d’évaluation

L’évaluation des offres se fera en trois(03) étapes :

- 1ère étape : Vérification de la présence et conformité du dossier administratif de chaque soumissionnaire ;

- 2ème étape : Analyse des offres techniques

- 3eme etape : Analyse des offres financières

Les critères d’évaluation des offres sont les suivants:

Sous peine de rejet, les pièces du dossier administratif requises doivent être produites en originaux ou en copies certifiées conformes par le service émetteur ou l’autorité administrative compétente, conformément aux dispositions du Règlement Particulier de l’Appel d’Offres. Elles doivent dater de moins de trois (03) mois ou avoir été établies postérieurement à la date de signature de l’avis d’Appel d’Offres.

En cas d’absence ou de non-conformité d’une pièce du dossier administratif lors de l’ouverture des plis, après un délai de 48 heures accordé par la Commission, l'offre sera rejetée.

NB : Les originaux des pièces administratives doivent être présentés pour vérification lors de la séance d'ouverture des plis

###### 14.1-Critères éliminatoires

- Absence ou insuffisance de la caution provisoire de soumission (CDEC);

- Absence de certificat de catégorisation délivré par l'Autorité chargée des marchés publics.

- Absence d’autres documents administratifs pertinents ou Essentials (non fourni après 48 hrs);

- Absence d’un certificat de catégorisation du MINMAP

- Fausses déclarations ou pièces falsifiées ou pièces scannées;

- Omission d’un prix quantifié dans le devis

- Non satisfaction d’au moins 75% des critères essentiel requis.

- Délai de livraison supérieur au délai prescrit ;

- Figurant sur la liste des entreprises suspendues du MINMAP

###### 14.2 Critères essentiels

L’évaluation sera faite sur la base des critères techniques prédéfinis pour une note globale de 100 points. Ces critères ont été groupés par rubriques ainsi qu’il suit:

- Présentation générale;

- Capacité financière;

- Sécurité sur le site;

- Rapport de visite du site par l’entreprise;

- Parapher et signer les dernières pages des clauses techniques et administratives particulières;

###### Attribution

Le contrat sera attribué au soumissionnaire dont l’offre est conforme pour l’essentiel aux dispositions du Dossier d’Appel d’Offres, et qui a présenté l’offre évaluée la moins-disant et techniquement qualifiée, conformément à l’article 99 du Code des marchés Publics.

###### Durée de validité des offres

Les soumissionnaires restent engagés par leurs offres pendant une période de quatre -vingt -dix (90) jours, à compter de la date limite fixée pour la remise des offres.

###### Renseignements complémentaires

Les renseignements complémentaires peuvent être obtenus tous les jours aux heures ouvrables auprès des services de la

Commission  de Passation des Marchés de la Commune de Limbe III dans la salle de délibération de l’Hôtel

de Ville de la Commune sise à Chop Farm - Bimbia.

LIMBE III, le 04/03/2026

Le Maire de la Commune de Limbe III

Le Maitre d’Ouvrage

Copies :

- Préfet du Fako,

- MINMAP/DD-Fako,

- ARMP/SW,

- Présidents CPM ;

- Affichage.

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

# TENDER FILE

##### CONTRACTING AUTHORITY:

THE MAYOR OF LIMBE III COUNCIL

##### TENDER BOARD:

LIMBE III COUNCIL INTERNAL TENDERS BOARD

TENDER FILE

No. 009/ONIT/LIIIC/L3C.TB/2026 OF 04/03/2026

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

(Emergency procedure)

#### FINANCING: PIB 2026 MINEE. BUDGETARY RECORD NO:

###### DOCUMENT No.2

General Regulations of the Invitation to Tender

##### CONTENTS

###### General

Article 1: Scope of the tender………………………………………………………. Article 2: Financing…………………………………………………………………… Article 3: Fraud and corruption………………………………………………………. Article 4: Candidates admitted to compete…………………………………………

Article 5: Building materials, materials, supplies, equipment and authorised services… Article 6: Qualification of the bidder…………………………………………………

Article 7: Visit of site of works………………………………………………………

- Tender File…………………………………………………………………………… Article 8: Content of Tender File………………………………………………………. Article 9: Clarifications on Tender File and complaints ………………………… Article 10: Modification of the Tender File…………………………………………

###### Preparation of Bids

Article 11: Tender fees……………………………………………………………… Article 12: Language of bid………………………………………………………… Article 13: Constituent documents of the bid……………………………………… Article 14: Amount of bid…………………………………………………………… Article 15: Currency of bid and payment………………………………………….. Article 16: Validity of bids…………………………………………………………… Article 17: Bid bond………………………………………………………………….. Article 18: Varying proposals by bidders…………………………………………… Article 19: Preparatory meeting to the establishment of bids……………………. Article 20: Form and signature of bids………………………………………………

- Submission of bids………………………………………………………………… Article 21: Sealing and marking of bids……………………………………………. Article 22: Date and time-limit for submission of bids……………………………. Article 23: Out of time-limit bids……………………………………………………. Article 24: Modification, substitution and withdrawal of bids…………………….

- Opening and evaluation of bids ………………………………………………… Article 25: Opening of bids…………………………………………………………. Article 26: Confidential nature of the procedure…………………………………… Article 27: Clarifications on the bid and contact with Contracting Authority……. Article 28: Determination of their compliance……………………………………. Article 29: Qualification of the bidder………………………………………………. Article 30: Correction of errors………………………………………………………. Article 31: Conversion into a single currency……………………………………… Article 32: Evaluation of financial bids…………………………………………… Article 33: National preference………………………………………………………

- Award of the Jobbing Order………………………………………………………………. Article 34: Award………………………………………………………………………

Article 35: Right of the Contracting Authority to declare an invitation to tender unsuccessful or to cancel a procedure……………………………….

Article 36: Notification of the award of the Jobbing Order……………………………… Article 37: Signature of the Jobbing Order………………………………………………… Article 38: Final bond………………………………………………………………….

###### General

Article 1: Scope of the tender:

  - . The Delegated Contracting Authority as defined in the Special Regulations of the invitation to tender hereby launches an open national invitation to tender for the works described in the Special Regulations.

  - The bidder retained or the preferred bidder must complete the works within the time- limit indicated in the Special Regulations and which time-limit runs from the date of notification of the Administrative Order or that indicated in the said Administrative Order.

  - In this Tender File, the term “day” means a calendar day.

Article 2: Financing: The source of financing of the works forming the subject of this invitation to tender shall be specified in the Special Regulations.

###### Article 3: Fraud and corruption:

  - The Delegated Contracting Authority requires of bidders and contractors the strict respect of rules of professional ethics during the award and execution of public contracts. By virtue of this principle:

- The following definitions shall be admitted:

  - Shall be guilty of “corruption” whoever offers, gives, requests or accepts any advantage in view of influencing the action of a public official during the award or execution of a contract;

  - Is involved in “fraudulent man oeuvres” whoever deforms or distorts facts in order to influence the award or execution of a contract;

  - “Collusive practices” shall mean any form of agreement between two or among several bidders (whether the Contracting Authority is aware or not) aimed at artificially maintaining the prices of bids at levels not corresponding to those resulting from competition;

  - “Coercive practices” shall mean any form of harm against persons or their property or threats against them in order to influence their action during the award or execution of a contract.

- Any proposed award shall be rejected if it is proved that the proposed preferred bidder is directly or through an intermediary, guilty of corruption or is involved in fraudulent manoeuvres, collusive or coercive practices for the award of this contract.

  - The Minister Delegate at the Presidency in charge of public contracts may, as a precaution, take a decision of exclusion from bidding for a period not exceeding two (2) years against any bidder found guilty of influence peddling, of conflicts of interest, insider trading, fraud, corruption or production of non-genuine documents in the bid, without prejudice to criminal proceedings that may be brought against him

###### Article 4: Candidates allowed for competing:

  - If the invitation to tender is restricted, consultation is addressed to all candidates retained after a pre-qualification procedure.

  - Generally, the invitation to tender is addressed to all entrepreneurs, subject to the following provisions:

- A bidder (including all members of a group of enterprises and all sub-contractors to the bidder) must be from an eligible country, in accordance with the funding agreement.

- A bidder (including all members of a group of enterprises and all sub-contractors to the bidder) must not be in a situation of conflict of interest, subject to disqualification. A bidder shall be judged to be in a situation of conflict of interest if he:

  - Is or was associated in the past with an enterprise (or a subsidiary of this enterprise) which provided consultancy services for the conception, preparation of specifications and other documents used within the scope of contracts awarded for this invitation to tender; or

  - Presents more than one bid within the context of invitation to tender, except authorized variants according to article 17, where need be; meanwhile, this does not prevent the participation of sub-contractors in more than one bid.

  - The Contracting Authority or Project Owner has financial interests in the capital in a way as to compromise the transparency of the procedures of award of public contracts.

- The bidder must not have been excluded from bidding for public contracts.

- A Cameroonian public enterprise may participate in the consultation if it can demonstrate that it is (i) legally and financially autonomous, (ii) managed according to commercial laws and (iii) not under the direct supervisory authority of the Contracting Authority or Project Owner.

###### Article 5: Building materials, materials, supplies, equipment and authorized services:

  - Building materials, the contractor’s materials, supplies, equipment and services forming the subject of this contract must originate from countries meeting the criteria of origin defined in the Special Regulations of the invitation to tender and all expenditure done within the context of the contract shall be limited to the said building materials, materials, supplies, equipment and services.

  - Within the meaning of this 5.1 above, the term “originate” shall designate the place where the goods are extracted, cultivated, produced, manufactured and from where the services originate.

  - The said material most be duly verified by the competent state engineer

###### Article 6: Qualification of bidder:

  - As an integral part of their bid, bidders must:

    - Submit a power of attorney making the signatory of the bid bound by the bid; and

    - Provide all information (complete or update information included in their request for pre-qualification which may have changed in the case where the candidates took part in pre-qualification) requested of bidders in the Special Regulations of the invitation to tender, in order to establish their qualification to execute the contract.

Where necessary, bidders should provide information relating to the following points:

- The production of certified balance sheets and recent turnovers;

- Access to a line of credit or availability of other financial resources;

- Orders acquired and contracts awarded;

- Pending litigations; and

- Availability of indispensable equipment.

  - Bids presented by two or more associated undertakings (Joint-contracting) must satisfy the following conditions:

- The bid must include all the information listed in article 6(1) above. The Special Regulations must indicate the information to be furnished by the group and that to be furnished by each member of the group;

- The bid and the contract must be signed in a way that is binding on all members of the group;

- The nature of the group (Joint or several) must be specified in the Special Regulations and justified with the production of a Joint venture agreement in due form;

- The member of the group designated as the representative will represent all the undertakings vis à vis the Project Owner and Contracting Authority with regard to the execution of the Contract;

- In case of Joint co-contracting, the co-contractors shall share the sums which are paid by the Project Owner into a single account. On the other hand, each undertaking is paid into its own account by the Project Owner where it is Joint co-contracting.

  - Bidders must equally present sufficiently detailed proposals to demonstrate that they comply with the technical specifications and execution time-limits set in the Special Regulations of the invitation to tender.

  - Bidders requesting to benefit from the margin of preference must furnish all the necessary information to prove that they satisfy the eligibility criteria set in article 33 of the General Regulations of the invitation to tender.

###### Article 7: Visit of works site:

  - The bidder is advised to visit and inspect the site and its environs and obtain by himself and under his own responsibility, all the information which may be necessary for the preparation of the bid and the execution of the works. The related cost of the visit of the site shall be borne by the bidder.

  - The Project Owner shall authorize the bidder and his employees or agents to enter the premises and the land for the said visit but only on the express condition that the bidder, his employees and agents free the Project Owner, his employees and agents of any responsibility that may ensue and indemnify them if necessary and that they shall remain responsible for any deadly or corporal accident, loss or material damages, costs and fees incurred from this visit.

  - The Project Owner may organize a visit of the site of the works during the preparatory meeting to establishing the bids mentioned in article 19 of the General Regulations of the invitation to tender.

##### TENDER FILE

###### Article 8: Content of Tender File:

  - The Tender File describes the works forming the subject of the contract, sets the consultation procedure of contractors and specifies the terms of the contract. Besides the addendum (addenda) published in accordance with article 10 of the General Regulations of the invitation to tender, it includes the following documents:

Document No. 1.The letter of invitation to tender. Document No. 2. The tender notice;

Document No. 3. The General Regulations of the invitation to tender; Document No. 4. The Special Regulations of the invitation to tender; Document No. 5. The Special Administrative Conditions; Document No. 6. The Special Technical Conditions;

Document No. 7. The schedule of unit prices; Document No. 8. The bill of quantities and estimates; Document No. 9. The sub details of unit prices; Document No. 10. Model documents of the contract:

- The execution schedule;

- Model of forms presenting the equipment, personnel and references;

- Model bidding letter;

- Model bid bond;

- Model final bond;

- Model of bond of start-off advance;

- Model of guarantee in replacement of the retention fund;

- Model contract;

Document No. 11. Models to be used by bidders;

- Model contract;

Document No. 12. Justifications of preliminary studies; to be filled by the Project Owner or Delegated Project Owner;

Document No. 13. List of first grade banking establishments or financial institutions approved by the Minister in charge of Finance authorized to issue bonds for public contracts to be inserted by the Contracting Authority.

  - The bidder must examine all the regulations, forms, conditions and specifications contained in the Tender File. It is up to him to furnish all the information requested and prepare a bid in compliance with all aspects of the said file.

###### Article 9: Clarifications on the Tender File and complaints

  - Any bidder who wants to obtain clarifications on the Tender File may request them from the Contracting Authority in writing or by electronic mail (fax or e-mail) at the Contracting Authority’s address indicated in the Special Regulations of the invitation to tender and send a copy to the Project Owner. The Contracting Authority replies in writing to any request for clarification received at least fourteen (14) days prior to the deadline for the submission of bids. A copy of the Contracting Authority’s response, indicating the question posed but not mentioning the author, is addressed to all bidders who bought the Tender File.

  - Between the publication of the tender notice including the pre-qualification phase of candidates and the opening of bids, any bidder who feels aggrieved in the public contracts award procedure may lodge a complaint to the Minister in charge of Public Contracts.

  - A copy of the complaint should be addressed to the Contracting Authority and to the body in charge of the regulation of public contracts and the chairperson of the Tenders Board.

  - The Contracting Authority has five (5) days to react. A copy of the reaction shall be forwarded to MINMAP and the body in charge of the regulation of public contracts.

###### Article 10: Amendment of the Tender File

  - The Contracting Authority may at any moment, prior to the deadline for the submission of bids and for any reason, be it at his initiative or in reply to a request for clarification formulated by a bidder, amend the Tender File by publishing an addendum.

  - Any published addendum shall be an integral part of the Tender File, in accordance with article 8.1 of the General Regulations of the invitation to tender and must be communicated in writing or made known by a traceable means to all bidders who bought the Tender File.

In order to give bidders sufficient time to take account of the addendum in the preparation of their bids, the Contracting Authority may postpone as is necessary, the deadline for the submission of bids, in accordance with provisions of article 22 of the General Regulations of the invitation to tender.

##### C PREPARATION OF BIDS

Article 11: Tender costs: The candidate shall bear the costs related to the preparation and presentation of his bid and the Contracting Authority and the Project Owner shall in no case be responsible for these costs nor pay for them whatever the evolution or outcome of the invitation to tender procedure.

Article 12: Language of bid: The bid as well as any correspondence and any document exchanged between the bidder and the Contracting Authority shall be written in English or French. Complementary documents and the forms provided by the bidder may be written in another language on condition that a precise translation into either English or French of the passages concerning the bid is included; in which case for reasons of interpretation, the translation shall be considered to be authentic.

###### Article 13: Constituent documents of the bid

  - The bid presented by the bidder shall include the documents detailed in the Special Regulations of the invitation to tender, duly filled and put together in three volumes:

- Volume 1: Administrative file: It includes:

  - All documents attesting that the bidder:

    - Has subscribed to all declarations provided for by the laws and regulations in force;

    - Paid all taxes, duties, contributions, fees or deductions of whatever nature;

    - Is not winding up or bankrupt;

    - Is not the subject of an exclusion order or forfeiture provided for by the law in force;

  - The bid bond established in accordance with the provisions of article 17 of the General Regulations of the invitation to tender;

  - The written confirmation empowering the signatory of the bid to commit the bidder, in accordance with the provisions of article 6(1) the General Regulations of invitation to tender.

- Volume 2: Financial bid: The Special Regulations specify the elements that will help in justifying the cost of the works, namely:

- The signed and dated original bid prepared according to the attached model, stamped at the prevailing rate;

- The duly filled Unit Price Schedule;

- The duly filled detailed estimates;

- The sub-details of prices and/or breakdown of all-in prices;

- The projected schedule of payments, where need be.

In this regard, the bidders will use the documents and models provided in the Tender File, subject to the provisions of article 17(2) of the General Regulations of the invitation to tender concerning the other possible forms of guarantees.

  - If in accordance with the provisions of the Special Regulations of the invitation to tender, the bidders present bids for several lots of the same invitation to tender, they could indicate rebates offered in case of award of more than one lot.

###### Article 14: Bid price:

  - Except otherwise stated in the Tender File, the amount of the contract shall cover all the works described in article 1.1 of the General Regulations of the invitation to tender, on the basis of the price schedule and the detailed bill of quantities and estimates presented by the bidder.

  - The bidder shall fill the unit prices and totals of all items on the schedule and bill of quantities and estimates.

  - Subject to contrary provisions provided for in the Special Regulations and in the Special Administrative Conditions, all dues, taxes and fees payable by the bidder on grounds of the contract or on any other ground, thirty (30) days prior to the submission of the bids, shall be included in the prices and in the total amount of the bid presented by the bidder.

  - If a price revision/updating clause is provided for in the contract, the date of establishment of the initial price, as well as the price revision/updating conditions for the said price must be specified. This is with the understanding that any contract of duration less than one (1) year shall not be subject to price revision.

  - All unit prices must be justified by sub-details established in accordance with the structure proposed in document 8 of the Tender File.

###### Article 15: Currency of bid and payment

  - In case of international invitations to tender, the currencies of the bid shall follow the provisions of either Option A or Option B below, the applicable option being that retained in the Special Regulations of the invitation to tender.

  - Option A: The amount of the bid shall be entirely made in the national currency.

The amount of the bid, unit prices of the price schedule and the prices of the bill of quantities and estimates are completely made in CFA francs in the following manner:

- Prices shall be entirely drawn in the national currency. The bidder who intends to commit expenditures in other currencies for the execution of the works shall indicate in the annex to the bid the percentage(s) of the amount of the bid necessary to cover the needs in foreign currencies, without exceeding the maximum of the three currencies of member countries of the funding institution of the contract.

- The exchange rates used by the bidder to convert his bid into the national currency shall be specified by the bidder in an annex to the bid in compliance with the specifications of the Special Regulations. These rates shall be applied for any payment within the framework of the contract so that the retained bidder does not bear any change in the exchange rate.

  - Option B: The amount of the bid shall be directly made in the national and foreign currency at the rates fixed in the Special Regulations.

The bidder shall draw the unit prices of the price schedule and the prices of the bill of quantities and estimates in the following manner:

a. The prices of inputs necessary for the works which the bidder intends to procure in the Contracting Authority’s country shall be in currency of the Contracting Authority’s country specified in the Special Regulations and called “national currency”;

a. The prices of inputs necessary for works which bidder intends to procure out of the Contracting Authority’s country shall be in the  currency of the country of origin of the bidder or of the currency of an eligible member country widely used in international trade.

  - The Contracting Authority may request the bidders to explain the needs in national and foreign currencies and to justify that the amounts included in the unit and total prices and indicated in annex to the bids are reasonable; to this end, a detailed statement of their needs in foreign currencies shall be furnished by the bidder.

  - During the execution of the works, most of the foreign currency to be paid as part of contract may be revised by mutual agreement between the Contracting Authority and the entrepreneur in a way as take account of any modification in the foreign currency needs within the context of the contract.

###### Article 16: Validity of bids:

  - Bids must remain valid during the period stated in the Special Regulations from the date of submission of the bids fixed by the Contracting Authority, in application of article 22 of the Special Regulations. A bid valid for a shorter period shall be rejected by the Contracting Authority or Contracting Authority as not being in compliance.

  - Under exceptional circumstances, the Contracting Authority may seek the approval of bidders to extend the validity time- limit. The request and the responses that will be given shall be in writing (or by fax). The validity of the bid bond provided for in article 17 of the General Regulations shall equally be extended for a corresponding duration. A bidder may refuse to extend the validity of his bid without losing his bid bond. A bidder who consents to an extension shall not be asked to modify his bid nor shall he be authorized to do so.

  - Where the contract does not include a price revision clause and that the period of validity of bids is extended by more than sixty (60) days, the amounts payable to the bidder retained shall be updated by application of the related formula featuring in the request for extension that the Contracting Authority addressed to bidders. The updating period shall run from the date of overrun of sixty (60) days to the date of notification of the contract or the Administrative Order for start of execution of works by the retained bidder, as specified in the Special Administrative Conditions. The effect of updating shall not be taken into account for purposes of evaluation of bids.

###### Article 17: Bid bond

  - In application of article 13 of the General Regulations, the bidder shall furnish a bid bond of the amount specified in the Special Regulations and which bid bond shall be a full part of his bid.

  - The bid bond must conform to the model presented in the Tender File; other models may be authorized subject to the prior approval of the Contracting Authority. The bid bond will remain valid for thirty (30) days beyond the original date set for the validity of bids or any other validity time-limit requested by the Contracting Authority and accepted by the bidder, in accordance with the provisions of article 16 (2) of the General Regulations.

  - Any bid without an acceptable bid bond shall be rejected by the Tenders Board as not in conformity. The bid bond of associated enterprises must be established in the name of the group submitting the bid and mention each member of the associated grouping.

  - The bid bonds of bidders who are not retained shall be returned within fifteen (15) days after publication of the award result.

  - The bid bond of the successful bidder shall be released as soon as the latter would have signed the contract and furnished the required final bond.

  - The bid bond may be seized:

- if the bidder withdraws his bid during the period of validity;

- if the retained bidder:

  - Fails in his obligation to register the contract in application of article 38 of the General Regulations;

  - Fails in his obligation to furnish the required final bond in application of article 38 of the General Regulations;

  - Refuses to receive notification of the Administrative Order to commence execution.

###### Article 18: Varying proposals of bidders

  - Where the works can be executed within variable deadlines, the Special Regulations shall specify these deadlines and shall indicate the method retained for the evaluation of the completion deadline proposed by the bidder within the specified deadlines. Bids that propose deadlines beyond those specified shall be considered as not being in conformity.

  - Except in the case mentioned in article 18(3) below, bidders wishing to offer technical variants must first assess the basic solution of the Contracting Authority as described in the Tender File and furnish in addition all the information which the Contracting Authority needs for a complete evaluation of the proposed variant, including the plans, calculations, technical specifications, sub-details of prices and proposed construction methods and all other useful information. If necessary, the Contracting Authority will examine only the technical variants of the bidder whose bid is in compliance with the basic solution has been evaluated as the lowest bid.

  - When according to the Special Regulations the bidders are authorized to directly submit the technical variants for certain parts of the works, these parts of the works must be described in the technical specifications. Such variants shall be evaluated on their own merit in accordance with the provisions of article 31(2) (g) of the General Regulations.

###### Article 19: Preparatory meeting to the establishment of bids

  - Except otherwise stipulated in the Special Regulations, a bidder may be invited to take part in a preparatory meeting which will hold at the date and place indicated in the Special Regulations.

  - The subject of the preparatory meeting shall be to furnish clarifications and answer any questions which may be raised at this stage.

  - As much as possible, the bidder is requested to submit any question in a way as to reach the Contracting Authority at least one week before the meeting The Contracting Authority may not reply to questions received too late. In this case, the questions and answers shall be transmitted according to the methods set in article 19(4) below.

  - The minutes of the meeting, including the text of the questions asked and the replies given, including questions prepared after the meeting, shall be forwarded immediately to everyone who bought the Tender File. Any modification of documents of the Tender File listed in article 8 of the General Regulations which may prove to be necessary at the end of the preparatory meeting shall be done by the Contracting Authority by publishing an addendum in accordance with the provisions of article 10 of the General Regulations and not through the minutes of the preparatory meeting.

  - The fact that a bidder does not attend a preparatory meeting for the establishment of bids shall not be a reason for disqualification.

###### Article 20: Form and signature of bid

  - The bidder shall prepare an original of the constituent documents described in article 13 of the General Regulations in a volume clearly indicated “ORIGINAL”. In addition, the bidder shall submit the number required in the General Regulations, bearing “COPY”. In case of discrepancy, the original shall be considered as authentic.

  - The original and copies of the bid must be typed or written in indelible ink (photocopies shall be accepted in the case of copies) and shall be signed by the person(s) duly empowered to sign on behalf of the bidder, in accordance with article 6(1a) or 6(2c) of the General Regulations, as the case may be. All the pages of the bid containing alterations or changes must be initialed by the signatory(ies) of the bid.

  - The bid shall bear no modification, suppression or alteration unless such corrections are initialed by the signatory (i.e.) of the bid.

##### D. SUBMISSION OF BIDS

###### Article 21: Sealing and marking of bids

  - The bidder shall seal the original and each copy of the bid in separate envelopes (internal envelopes) by marking on these envelopes “ORIGINAL” and “COPY”, as the case may be. The envelopes shall then be placed in another envelope which will equally be sealed but which will not give any indication regarding the identity of the bidder.

  - The external and internal envelopes:

- Should be addressed to the Contracting Authority at the address indicated in the Special Regulations;

- should bear the name and identification number of the project as indicated in the Special Regulations and bear the inscription “TO BE OPENED ONLY DURING THE BID-OPENING SESSION” as specified in the Special Regulations.

  - The internal envelopes should equally carry the name and address of the bidder in a way as to enable the Contracting Authority return the sealed bid if it is late in accordance with article 23 and 24 of the General Regulations.

  - If the external envelope is not sealed and marked as indicated in paragraphs 21(1) and 21(2) above, the Contracting Authority shall not be responsible if the bid is misplaced or opened prematurely.

###### Article 22: Date and time-limit for submission of bids

  - The bids must be received by the Contracting Authority at the address specified in article 21(2) of the Special Regulations not later than the date and time stated in the Special Regulations.

  - The Contracting Authority may, at his discretion, postpone the deadline set for the submission of the bids by publishing an addendum in accordance with the provisions of article 10 of the General Regulations. In this case, all the rights and obligations of the Contracting Authority and bidders previously governed by the initial date will henceforth be governed by the new date.

Article 23: Late bids: Any bid received by the Contracting Authority beyond the deadline for the submission of bids in accordance with article 22 of the General Regulations shall be declared late and consequently rejected.

###### Article 24: Modification, substitution and withdrawal of bids

  - A bidder may modify or withdraw his bid after submitting it, on condition that the written notification of the modification or withdrawal is received by the Contracting Authority prior to the end of the time-limit prescribed for the submission of the bids. The said notification must be signed by an authorized representative in application of article 20(2) of the General Regulations. The modification or the corresponding replacement bid must be attached to the written notification. As the case may be, the envelopes must bear the inscription “WITHDRAWAL”, and “REPLACEMENT BID” or “MODIFICATION”.

  - Notification of modification, replacement or withdrawal of the bid by the bidder should be prepared, sealed, marked and forwarded in accordance with the provisions of article 21 of the General Regulations. Withdrawal may equally be notified by telex but should in this case be confirmed by a duly signed written notification whose date, post mark being authentic, shall not be posterior to the time-limit set for the submission of bids.

  - In application of article 24(1), bids being requested to be withdrawn by bidders shall be returned to them unopened.

  - No bid may be withdrawn during the interval between the submission of bids and the expiry of the validity of bids specified by the model tender. The withdrawal of a bid by a bidder during this interval may lead to the confiscation of the bid bond in accordance with the provisions of article 17(6) of the General Regulations.

##### E. OPENING OF ENVELOPES AND EVALUATION OF BIDS

###### Article 25: Opening of envelopes and petitions

  - The Tenders Board shall open the envelopes in single phase and in the presence of the representatives of bidders who wish to attend at the date, time and address specified in the Special Regulations. Representatives of bidders shall sign a register attesting to their presence.

  - Firstly, envelopes marked “withdrawal” shall be opened and the contents announced to the hearing of everyone, while the envelope containing the corresponding bid shall be returned to the bidder unopened. Withdrawal shall be allowed only if the corresponding notification contains a valid empowerment of the signatory to request this withdrawal and if this notification is read to the hearing of everyone. Then the envelopes marked “Replacement bid” are opened and announced to the hearing of everyone and the new corresponding bid substituted for the preceding one which will be sent to the bidder concerned unopened. The replacement of the bid shall only be allowed if the corresponding notification contains a valid empowerment of the signatory requesting the replacement and read to the hearing of everyone. Lastly, the envelopes marked “modification” shall be opened and their contents read to the hearing of everyone with the corresponding bid. The modification of the bid shall only be allowed if the corresponding notification contains a valid empowerment of the signatory requesting the modification and read to the hearing of everyone. Only bids which were opened and announced to the hearing of everyone during the opening of bids shall then be evaluated.

  - All envelopes shall be opened successively and the name of the bidder announced aloud as well as the possible modification mentioned, the price offered, including any rebates [in case of opening of financial bids] and any variant, where necessary, the existence of a guarantee of the bid if it is required and any other details which the Contracting Authority deems useful to be mentioned. Only rebates and variants of bids announced to the hearing of everyone during the opening of bids shall be submitted for evaluation.

  - Bids (and modifications received in accordance with the provisions of article 24 of the General Regulations) which were not opened and read to the hearing of everyone during the bid-opening session for whatever reason, shall not be submitted for evaluation.

  - Bid-opening minutes are recorded on the spot mentioning the admissibility of bids, their administrative regularity, prices, rebates and time-limits as well as the composition of the Evaluation sub-committee. A copy of the said minutes to which is attached the attendance sheet is handed over to all the participants at the end of the session.

  - At the end of each bid-opening session, the chairperson of the Tenders Board immediately hands over to the focal point designated by the body in charge of regulation of public contract an initialed copy of the bids presented by bidders.

  - In case of petition as provided for by the Public Contracts Code, it should be addressed to the Minister Delegate in charge of Public Contracts with a copies to the body in charge of the regulation of public contracts, the head of structure to which is attached the Tenders Board concerned.

It must reach within a maximum deadline of three (3) working days after the opening of bids in the form of a letter to which is obligatorily attached a sheet of the petition form duly signed by the petitioner and possibly by the chairperson of the Tenders Board.

The Independent Observer attaches to his report the sheet that was handed to him, including any related commentaries or observations.

###### Article 26: Confidential nature of the procedure

  - No information relating to the examination, clarification, evaluation and comparison of bids and verification of the qualification of the bidders and the recommendation for the award shall be given to bidders or to any person not concerned with the said procedure as long as the preferred bidder has not been made public, subject to the disqualification of the bid of the bidder and suspension of the authors from all activities in the domain of public contracts.

  - Any attempt by a bidder to influence the Tenders Board or the Evaluation sub-committee of bids or the Contracting Authority in its award decision may lead to the rejection of his bid.

  - Notwithstanding the provisions of paragraph 26.2 above, between the opening of bids and the award of the contract, if a bidder wishes to enter into contact with the Contracting Authority for reasons having to with his bid may do so in writing.

###### Article 27: Clarifications on the bids and contact with the Contracting Authority

  - To ease the examination, evaluation and comparison of bids, the Tenders Board may, if it so desires, request any bidder to give clarifications on his bid. This request for clarification and the response thereto are formulated in writing but no change on the amount or content of the bid is sought, offered or authorized, except it is necessary to confirm the correction of calculation errors discovered by the Evaluation Sub-committee during the evaluation in accordance with the provisions of article 30 of the General Regulations.

  - Subject to the provisions of paragraph 1 above, bidders shall not contact members of the Tenders Board and the Evaluation Sub-committee for questions related to their bids, between the opening of envelopes and the award of the contract.

###### Article 28: Determination of compliance of bids

  - The Evaluation sub-committee shall carry out a detailed examination of bids to determine if they are complete, if the required guarantees are furnished, if the documents were correctly signed and if generally the bids are in proper order.

  - The Evaluation sub-committee shall determine if the bid is essentially in compliance with the conditions fixed in the Tender File based on the content without recourse to external elements of proof.

  - A bid that complies with the Tender File shall essentially be a bid that respects all the terms, conditions and specifications of the Tender File, without substantial divergence or reservation. A substantial divergence or reservation is that:

    - Which substantially limits the scope, quality or realization of the works;

    - which substantially limits, contrary to the Tender File, the rights of the Contracting Authority or his obligations in relation to the contract;

    - Whose correction would unjustly affect the competitiveness of the other bidders who presented bids that essentially complied with the Tender File

  - If a bid is essentially not in compliance, it shall be rejected by the competent Tenders Board and shall not subsequently be rendered in compliance.

  - The Contracting Authority reserves the right to accept or reject any modification, divergence or reservation. Modifications, divergences, variants and other factors which are beyond the requirements of the Tender File shall not be considered during the evaluation of bids.

Article 29: Qualification of the bidder: The Evaluation sub-committee shall ensure that the successful bidder retained for having submitted a bid substantially in compliance with the provisions of the Tender File, fulfills the qualification criteria stipulated in article 6 of the Special Regulations. It is essential to avoid any arbitrariness in determining qualification.

###### Article 30: Correction of errors

  - The Evaluation sub-committee shall verify bids considered essentially in compliance with the Tender File to correct the possible calculation errors. The Evaluation sub-committee shall correct the errors in the following manner:

- Where there is an incoherence between the unit price and the total obtained by multiplying the unit price by the quantity, th e unit price being authentic, the total price shall be corrected, unless the Evaluation sub-committee judges that it is a gross error of decimal point in the unit price in which case the total price as presented shall be authentic and the unit price corrected.

- If the total obtained by addition or subtraction of the totals is not exact, the sub totals shall be considered authentic and the total corrected.

- Where there is a difference between the price indicated in letters and in figures, the amount in letters shall be considered authentic, unless the amount is linked to an arithmetical error confirmed by the sub-detail of the said price, in which case the amount in figures shall prevail subject to paragraphs (a) and (b) above.

  - The amount featuring in the bid shall be corrected by the Evaluation sub-committee, in accordance with the error correction procedure above and with confirmation by the bidder, the said amount shall be deemed to commit him.

  - If the bidder who presented the bid evaluated as the lowest refuses the correction thus carried out, his bid shall be rejected and the bid bond may be seized.

###### Article 31: Conversion into a single currency

  - To facilitate the evaluation and comparison of bids, the Evaluation sub-committee shall convert the prices of bids expressed in various currencies into those in which the bid is payable in CFA francs.

  - The conversion shall be done using the selling rate fixed by the Bank of Central African States (BEAC) under the conditions defined by the Special Regulations.

###### Article 32: Evaluation and comparison of financial bids

  - Only bids considered as being in compliance, as per the provisions of article 28 of the General Regulations, shall be evaluated and compared by the Evaluation sub-committee.

  - By evaluating the bids, the Evaluation Sub-committee shall determine for each bid the evaluated amount of the bid by rectifying the amount as follows:

- By correcting any possible error in accordance with the provisions of article 30.2 of the General Regulations;

- By excluding projected sums and where necessary provisions for unforeseen occurrences featuring in the bill of quantities and estimates but by adding the amount of works done under State supervision where they are costed in a competitive manner as specified in the Special Regulations.

- By converting into a single currency the amount resulting from the rectifications (a) and (b) above, in accordance with the provisions of article 31(2) of the General Regulations;

- By appropriately adjusting any other modification, divergence or quantifiable reservation on technical or financial basis.

- By taking into consideration the various execution time-limits proposed by the bidders, if they are authorized by the Special Regulations;

- If need be, in accordance with the provisions of article 13(2) of the General Regulations and the Special Regulations by applying the rebates offered by the bidder for the award of more than one lot, if this invitation to tender is launched simultaneously for several lots.

- If need be, in accordance with the provisions of article 18(3) of the Special Regulations and the Technical Specifications, the proposed technical variants, if they are permitted, shall be evaluated on their own merit and independently of the fact that the bidder offered or not a price for the technical solution specified by the Contracting Authority in the Special Regulations.

  - The estimated effect of price revision formulae featuring in the GAC and SAC applied during the period of execution of the contract shall not be considered during the evaluation of bids.

  - If the bid judged the lowest bid is considered abnormally low or strongly unbalanced in relation to the estimates of the Project Owner for the works to be executed in this contract, the Tenders Board may, from the sub-details of prices furnished by the bidder for any element or all the elements of the bill of quantities and estimates, verify if these prices are compatible with the construction methods and proposed calendar. In the case where the justifications presented by the bidder are not satisfactory, the Contracting Authority may reject the bid after the technical opinion of the Public Contracts Regulatory Agency.

Article 33: Preference granted national bidders: National contractors shall benefit from a margin of national preference during the evaluation of bids as provided for in the Public Contracts Code.

###### Article 34: Award

  - The Contracting Authority shall award the contract to the bidder whose bid was judged essentially in compliance with the Tender File and who has the required technical and financial capacities to execute the contract satisfactorily and whose bid was evaluated as the lowest by including, where necessary, proposed rebates

  - If, according to article 13(2) of the General Regulations, the invitation to tender comprises several lots, the lowest bid shall be determined by evaluating this contract with other lots to be awarded concurrently, by taking into account the rebates offered by the bidders in the case of more than one lot.

  - Any award of contract shall be made to the bidder fulfilling the technical and financial capacities required resulting from t he evaluation criteria and presenting the bid evaluated as the lowest.

Article 35: The right by the Contracting Authority to declare an invitation to tender unsuccessful or cancel a procedure: The Contracting Authority reserves the right to cancel a procedure of invitation to tender after the authorization of the Minister Delegate at the Presidency in charge of Public Contracts where the bids have been opened or to declare an invitation to tender unsuccessful after the advice of the competent Tenders Board, without any claims being entertained.

Article 36: Notification of award of the contract: Before the expiry of the validity of the bids set in the Special Regulations, the Contracting Authority shall notify the preferred bidder by telecopy confirmed by registered mail or by any other means that his bid was retained. This letter will indicate the amount the Project Owner will pay the contractor to execute the works and the execution time-limit.

###### Article 37: Publication of results of award and petitions

  - The Contracting Authority shall communicate to any bidder or administration concerned, upon request addressed to it within a maximum deadline of five (5) days after publication of the award results, the Independent Observer’s report as well as the minutes of the award session of the related contract to which shall be attached the evaluation report of the bids.

  - The Contracting Authority is bound to communicate the reasons for the rejection of bids of the bidders concerned who so request.

  - After publication of the award results, bids that are not withdrawn within fifteen (15) days shall be destroyed, without any claims for compensation being entertained. Only the copy destined for the body in charge of regulation shall be kept.

  - In case of petition, it should be addressed to the Public Contracts Authority, with copies to the body in charge of the regulation of public contracts, the Contracting Authority and the chairperson of the Tenders Board concerned. It must take place within a maximum deadline of five (5) working days after the publication of the results.

###### Article 38: Signing of the contract

The contract must be notified to the successful bidder within five (5) days of its date of signature.

###### Article 39: Final Bond

  - Within twenty (20) days of the notification by the Contracting Authority, the contractor shall furnish the Project Owner with a final bond, to guarantee the complete execution of the works.

  - The bond whose rate varies between 2 and 5 percent of the amount of the contract inclusive of all taxes, may be replaced by a guarantee from a banking establishment approved according to the instruments in force with the Project Owner as beneficiary or or several guarantee.

  - Small and medium-sized enterprises (SME) constituted of national capital and managed by nationals may, in lieu of the guarantee, provide a statutory lien or a bond issued by a banking establishment or first rate financial institution approved in accordance with the instruments in force.

  - Failure to produce the final bond within the prescribed time limit shall likely cause the termination of the contract under the terms laid down.

###### DOCUMENT No.3

PARTICULAR REGULATIONS OF THE INVITATION TO TENDER

Article 00: DEFINITIONS AND DUTIES UNDER THE INVITATION TO TENDER

- DELEGATED CONTRACTING AUTHORITY: THE MAYOR – LIMBE III COUNCIL

-DELEGATED PROJECT OWNER: THE MAYOR – LIMBE III COUNCIL

-CONTRACT ENGINEER: THE DIVISIONAL DELEGATE WATER RESOURCES AND ENERGY - MINEE

-CONTRACT MANAGER: THE CHIEF OF TECHNICAL SERVICE – CDO – LIMBE III COUNCIL.

-OFFICIALS RESPONSIBLE FOR UNANNOUNCED CONTROLS OF THE EXECUTION: THE CONTROL BRIGADE MINMAP - FAKO

-CONTRACTORS: TO BE SELECTED THROUGH THIS ONIT.

###### ARTICLE 1: Definition of Works

Within the framework of the execution of the 2026 state budget, the Mayor of Limbe III Council hereby launches an OPEN NATIONAL INVITATION TO TENDER N°009/ONIT/LIIIC/FAKO/L3C.TB/PIB2026 of 04/03/2026 FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY.

###### ARTICLE 2: Execution Dateline

The maximum completion period of the works to the state of provisional reception is three (03) months and counting from the date of notification of the service order to start work

###### ARTICLE 3: Source of funding

The works which form the subject of this open national invitation to tender shall be financed by the Public Investment Budget of the Republic of Cameroon for the 2026 fiscal year, allotted to the authorizing officer.

###### Article 4: Consistency of the bids

The bid shall include a file for:

###### Envelope A: Administrative documents

It shall consist of the following documents, stapled and arranged in the following order.

- A Declaration of intention to tender stamped, dated and signed by the bidder or group representative in conformity with the model attached.

- An attestation of non-bankruptcy (not older than 03 months), issued by the court of competent jurisdiction of the place of residence of the bidder.

- An attestation of domiciliation: Bank account in the name of the enterprise issued by a bank or any first-order credit institution approved by the Minster in charge of finance.

- Bid bond from CDEC (bank guarantee) as indicated on the tender notice

- Treasury Receipt showing the payment of the tender fee as stipulated in the tender notice.

- An attestation of CNPS: current (not older than 03 months) certificate from the National Social Insurance Fund (CNPS) certifying that the bidder has effectively paid his/her social contributions and destined for this tender

- Certificate of non-exclusion attesting that the bidder is not the subject of a temporary or permanent exclusion from Public Contracts, not older that three (03) months issued by ARMP.

- Attestation of fiscal conformity certifying that the bidder owes no taxes signed by the director or the head of tax center.

- A certified copy of valid Tax payer’s card;

- Plan and attestation of localization;

- A copy of business registration;

- Attestation of site visit; signed by the bidder on honor with photos of the site and counter signed by the project owner.

- Group agreement; as the case may be.

- Power of attorney; signed by a notary or bailiffs

- Certificate of Categorization; by MINMAP

N.B: All documents shall be originals as requested or certified true copies legalized by competent services or that which issued them and must not be more than three (03) months old.

N.B: Absence of the following documents shall results to outright rejection

- Receipt for the purchase of tender file

- Bid bond

##### a category D certificate of categorization from MINMAP;

- All bids not containing all the documents listed above or not in conformity with the models shall be simply rejected

The documents shall be arranged in the order listed above and separated from each other by color separators different from white.

Any document with double certification shall not be accepted.

#### Envelope B: TECHNICAL FILE

It shall contain the documents cited below and placed in the following order:

| No | DOCUMENT | OPERATION REQUESTED | AUTHENTICATION |
| --- | --- | --- | --- |
| B1 | Personnel list | It shall contain: - Works Supervisor: at least a holder of Degree in Civil Engineering with at least 5 years’ experience in the field of construction or rehabilitation - Foreman: at least a holder of BAC F4 (Civil Engineering) with at least 5 years’ experience in the domain of Construction. - Mason; at least BAC in Building construction/masonry and at least 03 years of experience - Electrician; at least HND in electricity or Equivalent and at least 03 years of experience | Attach for each person a - CV signed and dated. - Certified copy of certificate - Attestation of Presentation of originals - Certified copy of valid ID card with 03 signatures of bearer (all key personnel must present a commitment of availability duly signed) |
| B1 | Organisation of works/ methodology | In conformity with article 7 below, it shall show clearly the organization of the enterprise ( methodology of execution, work schedule, site installation, supply of materials, etc) | Date, signature and stamp of bidder at the end of each document |
| B3 | Sub-Contracting | Information on the sub-Contract (equipment, personnel, references, etc) | Date and signature of sub- Contract. (only 30% of the contract may be sub- Contracted) |
| B4 | Attestation of site visit | Attestation of visit to the site where the works are to be carried out signed by the bidder on honour. A site visit report signed by contractor or works supervisor. ( see attached format) | Dated and signed by the Contractor by honour. |
| B5 | Financial capability | Attestation of pre-financing of an amount minimum 55% of the bid amount delivered by a banking institution recognized by MINFI/COBAC | Date and signature of bank Manager in charge. |
| B6 | Technical specifications | Provided in tender file. | Initialed on every page and Signed and stamped on the last page. |

The documents shall be arranged in the order listed above and separated from each other by color separators different from white.

##### ENVELOPE B: FINANCIAL OFFER

| No | DOCUMENT | OPERATION REQUESTED | AUTHENTICATION |
| --- | --- | --- | --- |
| C1 | The tender | Format to be completed and tender amount inserted. | Signature, date and stamp of bidder. A Fiscal stamp of 1500 FCFA. |
| C2 | Unit Price Elaboration | Format to be completed showing detail breakdown of prices. | Initials on each page, all pages stamped. |
| C3 | Bill of Quantities and Cost Estimates | Format to be completed. | Initials on each page, signature on last page, all pages stamped. |
| C4 | Price enclosure Slip | Format to be completed showing the unit prices. | Initials on each page and signature on last page, all pages stamped with enterprise function stamp. |

All these documents are to be arranged in the above order and separated with colour Separators other than white.

###### Building materials, materials, supplies equipment and authorized services.

The taxes and duties on the importation of materials for execution of works shall be in conformity with the legislation of the Republic of Cameroon.

###### Article 5: Main eliminatory and qualification criteria of bidders 5.1-Eliminatory criteria

- Absence or insufficient bid bond from CDEC;

- Deadline of execution more than the prescribed;

- Absence of a Certificate of categorization;

- False declaration or falsified or scanned or forged documents;

- Omission of a quantified task on the bill of quantities and cost estimates

- Enterprise with an abandoned contract or uncompleted project (above contractual deadline with due justification) in the South West Region.

- Non satisfaction of at least 75% of the main qualification criteria

- Deadline for delivery higher than prescribed.

- Featuring on MINMAP’S list of suspended enterprises,

5.2. Main qualification criteria: The criteria relating to the qualification of candidates could indicatively be on the following:

- General presentation, compliance with the model bid,

- Financial capacity;

- Duration of execution;

- General presentation, compliance with the model bid;

- Methodology, organization of the site and relevance of proposed solutions;

- Safety at site;

- Site visit report from the contractor

- Initialed and sign last pages of special technical administrative clauses

##### ARTICLE 6: OBLIGATIONS AND CONDITIONS TO TENDER

  - Any bid that does not respect any of the conditions for tendering shall not be received.

  - After submission no bids shall be withdrawn, modified or corrected for any reason. This condition shall apply before and after the submission date.

##### ARTICLE 7: THE BIDDING DOCUMENTS

  - The documents that make up this tender are as follows: Document NO: 1: Invitation to Tender.

Document NO: 2: The General Tender Regulation Document NO: 3: The Special Tender Regulation

Document NO: 4: The Special Administrative Conditions (SAC/CCAG)

Document NO: 5: Specifications Technical Conditions (STC/CCTP) Document NO: 6: Form for Bill of Quantities and Cost Estimates (BQCE) Document NO: 7: Form for Unit Prices (PES)

Document NO: 8: Model Forms

    - General information Form

    - Submission Form

    - Bank Guarantee Forms (Bid bond, Guarantee retentions)

    - Form for Price Elaboration (Detail Pricing) (PE) Document NO: 9: Execution plans.

##### ARTICLE 8: AMENDMENT OF BIDDING DOCUMENTS

  - At any time prior to the dateline for submission of bids, the Regional Tenders Board, may modify the bidding documents for any reasons, whether at its own initiative, at the request of the Contracting Authority or in response to a clarification requested by a prospective bidder.

  - All prospective bidders that have received the bidding documents will be notified of all amendments in writing or be contacted by telephone to do so and all such modifications will be considered as an integral part of their bidding documents.

  - In order to allow prospective bidders reasonable time in which to take the amendment into account in preparing their bids, the Regional Tenders Board at its discretion, may extend the dateline for the submission of bids if there were any such amendments.

##### ARTICLE 9: CALCULATION OF PRICES

  - The amount shall be calculated on the bases of variable prices.

The bidder shall fill, in letters and in figures, the unit prices in the price enclosure slip and the unit prices are to be multiplied by the quantities given in order to obtain the amount of his/her offer for each item.

  - The price enclosure slip must be completed. Any price lacking on this form shall be considered as follows:

- The corresponding price on the bill of quantities and costs estimates;

- The highest corresponding price furnished by the bidder technically qualified, if it exist in the same lot,

- The average of all the prices of bidders in the same lot if the bidder is the only qualified one.

  - The bidder shall express the prices in the PES and BQCE in francs CFA excluding taxes before adding the taxes to the BQCE only.

The prices on the PES shall have priority over those of the BQCE and PE. They shall serve as the bases of calculation of the bidding amount.

The eventual calculation errors shall be corrected by the Sub Committee for Analysis and the amount altered if necessary without any complaints from the bidder.

##### ARTICLE 10: PRESENTATION OF BIDS

  - Signature of bids – Power of Attorney

    - All the signatures and initials needed for the tender and indicated in this article must be those of the bidder himself or his/her representative duly mandated.

    - If the bidder is a group of enterprises, each group member or representative must sign the bidding documents such that the result shall be a joint offer.

The group shall choose a common representative who shall receive Service Orders and carry out all transactions in the name of the group.

  - Presentation of bids

The bid shall be presented in seven (07) copies (one (01) original and six (06) copies) marked as such and put inside three (03) sealed envelopes comprising the following:

All these documents are to be arranged in the above order and separated with colour separators.

Note: Plans supplied with tender file should not be submitted.

##### SUBMISSION OF OFFERS AND OPENING OF BIDS

Envelopes A, B, a are to be sealed and each envelope shall be marked “ADMINISTRATIVE DOCUMENTS, FINANCIAL OFFER” as the case may be. The three envelopes shall be placed in a fourth envelope, sealed and shall carry the following inscriptions:

OPEN NATIONAL INVITATION TO TENDER

No. 009/ONIT/LIIIC/L3C.TB/2026 OF 04/03/2026

## FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

#### (BY EMERGENCY PROCEDURE)

(TO BE OPENED ONLY DURING THE BIDS OPENING SESSION)

All bids shall be deposited online using the Coles platform and a backup copy must be deposited at The Mayor’s office, at the office of the secretary of the Regional Tenders Board. Any bid opened prematurely shall be rejected and returned to the bidder.

##### ARTICLE 11: TECHNICAL PROPOSALS

Proposals for different variants can be accepted from the bidder but the bidder has the obligation of costing the variant in the tender file.

##### ARTICLE 11: BID BOND

The bidder shall furnish a bid bond from CDEC (provisional caution) of Three hundred and thirty thousand (330,000) francs CFA from a banking institution of the first order accredited by the Ministry in charge of Finance according to the criteria of COBAC.

##### ARTICLE 11: TENDER

Each bidder shall tender following the conditions laid down in this tender file.

##### ARTICLE 12: CURRENCY

The unit prices shall be calculated in Francs CFA, and furnish in figures and words without taxes, while the total amount shall be calculated without taxes and then with taxes according to the BQCE. The currency that shall be used for payment shall be the FCFA.

##### ARTICLE 13: PAYMENT MODALITIES

The CONTRACT shall be paid upon presentation of monthly installments “Décomptes” established from attachments signed by Project Manager and visa by the Contracting Authority showing the work progress, presented by the CONTRACT Engineer and countersigned by the Contract Manager (Authorizing Officer) and the CONTRACT.

##### ARTICLE 14: IMPORTATION OF MATERIALS

The taxes and duties on the importation of materials for execution of works shall be in conformity with the legislation of the Republic of Cameroon.

##### ARTICLE 15: VERIFICATION OF BIDS

  - The administration has a period of one (01) month to examine the bids and make its choice. It shall eventually rectify, as indicated in article 5.3, the bidding amount without any objection from the bidder.

  - At the request of the tender board, the bidder shall furnish in writing, within seven (07) calendar days, any information necessary for the examination of his/her bid or concerning errors and omissions noted.

  - The tender board reserves the right to summon the bidder at his/her expenditure for complementary explanations. Any errors discovered by the tender board shall be rectified as follows:

    - Where there exist a difference between the amount in figures and the amount in letters, the amount in letters shall be taken as correct;

    - Where there exist a difference between a unit price and the amount obtained by the product of unit price and the quantity, the unit price shall be taken, except the tender board estimates that it is an error of decimal point, in which case the amount is taken and the unit price corrected.

    - The sub-committee for the evaluation of bids, whose president shall be designated by the Regional Tenders Board, shall be constituted during the bid opening session

##### ARTICLE 16: VALIDITY OF BIDS.

The bidder shall be bound by his/her bid for a period of ninety (90) days from the day of submission of bids. If at the end of this period the CONTRACT is not notified to the bidder, he can withdraw his/her bid or accept the extension of duration on the written request of the administration.

The opening of bids shall take place on the date and place prescribed in the tender file. Envelopes received from prospective bidders shall be opened at once and evaluated in two stages.

- OPENING OF ENVELOPES (A) (B) and (C) (FIRST STAGE)

###### OPENING/EXAMINATION OF ENVELOPE (A):

(Administrative documents) shall be opened in public and the conformity of the documents shall be verified. The administrative documents must be complete, valid and authentic. The bid bond must conform to the format submitted. Only bids with documents that meet these requirements shall have their other envelopes evaluated.

- OPENING/EXAMINATION OF ENVELOPE (B);

(Technical Offer) shall be opened in public to determine whether the file is complete with the authenticity of documents checked and whether the documents are legalized by the competent services concerned and placed in the recommended order.

###### OPENING/EXAMINATION OF ENVELOPE (C);

(Financial Offer) shall be carried out only for bids that have sailed through the first two steps. Bids amounts shall be read out in public as inscribed in the financial offer of the bidder.

NB: Copies of the financial offer shall alongside the Administrative offer, be handed to a Sub-Technical committee for verification and evaluation.

NB:

The minimal technical acceptable mark is 100% of the technical mark, All bids having less than 100/100 of the technical marks shall be eliminated.

  - EVALUATION OF TECHNICAL OFFER

| A. General presentation of bids |  |
| --- | --- |
| - Presence of all documents ………………………………………….………….. | yes/no |
| - Properly bound………………………………………………………………............ | yes/no |
| -Is the Table of content coherent…………………………………………………… | yes/no |
| - Separators in colour apart from white…………………………………………… | yes/no |
| - Order prescribed respected………………………………………………………. | yes/no |
| - Clearness of the documents…………………………………………............... | yes/no |
| TOTAL 1 | /6 |
| B. Qualification of site personnel |  |
| - Organizational Chart of the enterprise………………………………………… | yes/no |
| - Organizational Chart of site with comments ……………………………….. | yes/no |
| Works Supervisor: Holder of at least a degree in Civil Engineering |  |
| - Certified copy of valid NIC bearing 03 signature of bearer… | yes/no |
| - Certified copy of Diploma of Works Director...………… | yes/no |

| - CV signed and dated by Works Director……………………………… | yes/no |
| --- | --- |
| - Professional experience of Works Director at least five years……………. | Yes/no |
| - Atleast 2 similar projects |  |
| - Attestation of presentation of original diploma of Works Director … | yes/no |
| Site foreman: Civil Engineering technician (holder of at least BAC F4 or equivalent) |  |
| - Certified copy of valid NIC bearing 03 signature of bearer………………….. | yes/no |
| - Certified copy of certificate of site Foreman...…………………………………… | yes/no |
| - CV signed and dated by site foreman………………………………………… | yes/no |
| - Professional experience of site foreman at least five years ……………… | yes/no |
| - Atleast 2 similar projects … | yes/no |
| mason; at least BAC in building construction/masonry and at least 03 yrs of experience |  |
| - Certified copy of valid NIC bearing 03 signatures of bearer………………….. | yes/no |
| - Certified copy of diploma | yes/no |
| - CV signed and dated | yes/no |
| Tiler; at least CAP in Civil Engineering or equivalent and at least 03 yrs of experience |  |
| - Certified copy of valid NIC bearing 03 signatures of bearer………………….. | yes/no |
| - Certified copy of diploma | yes/no |
| - CV signed and dated | yes/no |
| Painter; at least CAP in Civil Engineering or equivalent and at least 03 yrs of experience |  |
| - Certified copy of valid NIC bearing 03 signatures of bearer………………….. | yes/no |
| - Certified copy of diploma | yes/no |
| - CV signed and dated | yes/no |
| Electrician; at least HND in electricity and atleast 03 yrs of experience |  |
| - Certified copy of valid NIC bearing 03 signatures of bearer………………….. | yes/no |
| - Certified copy of diploma | yes/no |
| - CV signed and dated | yes/no |
| TOTAL 2 | /24 |
| C. The methodology of intervention and execution of work |  |
| - Site Visit report signed and dated by the bidder or dully authorized representation with photos of the site…………………... | yes/no |
| - Coherence Detailed technical note on the organization and execution of works… | yes/no |
| - Coherence synchronized Planning of execution of works…………………… | yes/no |

| Coherence of the General Security and Safety Plan (GSSP) within the building site………… | yes/no |
| --- | --- |
| - Coherence socio - environment measures for the site protection.. | yes/no |
| - Coherence in the organization of the site……………………….…………….. | yes/no |
| - Plan of supply of constructional materials and storage conditions…… | yes/no |
| - Coherence detailed manpower deployment plan……………………. | yes/no |
| -Technical note on the observations and recommendations……………. | yes/no |
| - CCTP dully initialled on each page, signed, dated and stamped on the last page | yes/no |
| -SAC and model contract each page, initial and signed | Yes/no |
| TOTAL 3 | /11 |
| e– Pre-financing |  |
| Attestation of credibility shall be at least 55% of the bid price.................... | yes/no |
| TOTAL 4 | /1 |
| TOTAL = TOTAL 1 + TOTAL 2+ TOTAL 3 + TOTAL 4 | /42 |

NB:

The minimal technical acceptable mark is 75% of the technical mark, i.e. 33/42. All bids having less than 75/100 of the technical marks shall be eliminated.

###### :	Evaluation of Financial Offer:

Careful study shall be carried out on the details of prices, unit prices, the bill of quantities and cost estimates presented to make sure the bidder did study the prices and has not made an arithmetic error to arrive at his/her final contract amount. The prices on the PES in words shall have priority over those of the BQCE and SDE. They shall serve as the bases of calculation of the bidding amount.

The eventual calculation errors shall be corrected by the Sub Committee for Analysis and the amount altered if necessary without any complaints from the bidder. Any laxity noticed at the study of prices shall lead to the disqualification of the bid.

##### :	CHOICE OF CONTRACTOR (CRITERIA OF AWARDING CONTRACT):

According to article 33(1) (a) of the Public Contract Code, the contract shall be awarded to the meritorious and lowest bidder, careful study must be carried out on the details of prices, unit prices, the bill of quantities and cost estimates presented to make sure the bidder did study the prices and has not made an arithmetic error to arrive at his/her final contract amount.

##### ARTICLE 18: PROCEDURE OF AWARD OF CONTRACT

The results from this tender shall be prepared, awarded and executed according to the rules and procedures defined by the legislation in force for Public contracts.

  - The winner shall be notified through his/her official address or public media. He shall in five (05) days fulfil the formalities related to the awards, especially to submit seven (07) copies of the proposed contract that he/she has completed and signed, to the office of the Delegated Contracting Authority for final signature.

  - In the case where the enterprise does not fulfill these conditions, his/her choice shall simply be annulled without further notice and the next contender shall be called in for replacement.

Once the Delegated Contracting Authority has signed the contract, the contractor shall be notified with immediate effect. He has three (03) days to contact the Authorizing Officer for the beginning of execution of works following notification of the Service Order to start work by the control Engineer. Failure to respect the date line shall call for withdrawal and eventual cancellation of contract.

  - The present contract can be cancelled outright in the cases provided for by Decree NO.:2004/275 of 24th September 2004 in the Public Contracts Code.

SPECIAL ADMINISTRATIVE CONDITIONS (SAC/CCAP)

##### CONTENT

CHAPTER I: GENERAL PROVISIONS

ARTICLE 1: AIM OF THE CONTRACT

ARTICLE 2: COMPOSITION OF DOCUMENTS OF THE CONTRACT ARTICLE 3: DEFINITIONS AND ATTRIBUTIONS

ARTICLE 4: REPRESENTATION AND DOMICILIATION OF THE ENTREPRENEUR ARTICLE 5: SERVICE ORDERS AND CORRESPONDENCES

##### CHAPTER II: EXECUTION OF WORKS

ARTICLE 6: KNOWLEDGE OF THE SITE AND GENERAL CONDITIONS OF WORKS ARTICLE 7: CONSISTENCY OF WORKS

ARTICLE 8: ROLE AND RESPONSIBILITY ARTICLE 9: DURATION OF EXECUTION ARTICLE 10: PLANNING OF WORKS

ARTICLE 11: PLANS AND DOCUMENTS OF EXECUTION ARTICLE 12: SUBCONTRACTING

ARTICLE 13: PENALTIES AND RESTRAINTS OF DELAY ARTICLE 14: RECEPTION OF WORKS

ARTICLE 15: OBLIGATION OF THE ENTREPRENEUR ARTICLE 16: INSURANCE

ARTICLE 17: DURATION OF GUARANTEE

##### CHAPTER III: FINANCIAL PROVISIONS

ARTICLE 18: THE AMOUNT OF THE CONTRACT ARTICLE 19: METHOD OF PAYMENT OF WORKS ARTICLE 20: BANKING DOMICILIATION ARTICLE 21: FINAL SECURITY BOND ARTICLE 22: GUARANTEE DEDUCTIONS ARTICLE 23: ADVANCE FOR STARTING ARTICLE 24: FISCAL AND CUSTOMS REGIME ARTICLE 25: SECURITY

ARTICLE 26: STAMP AND REGISTRATION

##### CHAPTER IV: OTHER PROVISIONS

ARTICLE 27: LITIGATIONS

ARTICLE 28: CASE OF FORCE-MAJEURE ARTICLE 29: TERMINATION

ARTICLE 30 AND LAST: VALIDITY

##### CHAPTER I: GENERAL PROVISIONS

Article 1: AIM OF THE CONTRACT.

The present Contract has as objective THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

By Emergency Procedure.

###### Article 2: Method of award

This Contract is awarded by urgent open national invitation to tender in accordance with decree NO: 2018/366 of 20th June 2018 to institute the Public Contracts Code and subsequent texts.

Article 3: COMPOSITION OF DOCUMENTS OF THE CONTRACT

The constituent contractual documents of the present contract are by order of priority:

###### Files of Particular Order

    - The present Notebook of Special Administrative Conditions (SAC/CCAP)

    - The Notebook of Special Technical Conditions (STC/CCTP)

    - The Quantitative and bill of estimates,

    - The Tender file

    - The Planning of works

###### - General Applicable instruments/legislation in force

This Jobbing order shall be governed by the following legal instruments:

- Law No92/007 of 14 August 1992 bearing on the Labour Code;

- Framework Law No. 96/12 of 5 August 1996 on the management of the environment;

- The Mining Code;

- Instruments governing the various professional bodies;

- Law No2002/003 of 19 April 2002 on the General Tax Code;

- Law No2018/011 of 11 July 2018 to lay down the Code of Transparency and Good Governance in the Management of Public Finance in Cameroon;

- Law No2018/012 of 11 July 2018 to establish the Fiscal Regime of the State and other Public Entities;

- Law No2021/026 of 16 December 2021 on the Finance law of the Republic of Cameroon for the 2022 financial year;

- Decree No. 2001/048 of 23 February 2001 relating to the setting up, organization and functioning of the Public Contracts Regulatory Agency

- Decree No. 2003/651/PM of 16 April 2003 to lay down the procedure for implementing the tax and customs system applicable to public contracts;

- Some provisions of Decree No. 2012/075 of 8 March 2012 to organise the Ministry in charge of Public Contracts;

- Decree No2012/076 of 8 March 2012 modifying and completing some provisions of Decree No2001/048 of 23 February 2001 relating to the setting up, organization and functioning of the Public Contracts Regulatory Agency;

- Decree No. 2018/366 of 20 June 2018 to institute the Public Contracts Code; and its subsequent application texts;

- The General Administrative Conditions applicable on works public contracts that went into effect by Order No. 033/CAB/PM of 13 February 2007;

- Circular No.0001877/C/MINFI of 31st December 2025 bearing on instructions relating to the Execution of Finance Laws, the Monitoring and Control of the Execution of the Budget of the State and other Public Entities, for the 2026 financial/fiscal year;

- Unified Technical Documents (DTU) for building works;

- Applicable technical standards in Cameroon or alternatively, French or European Standards in the domain;

- The texts governing the trades of the works covered by this jobbing order.

###### Article 4: DEFINITIONS AND ATTRIBUTIONS

For the application of the provisions of the present contract, it is specified that:

- CONTRACTING AUTHORITY: THE MAYOR OF LIMBE III COUNCIL.

-AUTHORISING OFFICER/PROJECT OWNER: THE MAYOR OF LIMBE III COUNCIL.

-CONTRACT ENGINEER: THE DIVISIONAL DELEGATE MINEE - FAKO

-OFFICIALS RESPONSIBLE FOR UNANNOUNCED CONTROLS OF THE EXECUTION: THE CHIEF OF CONTROL BRIGADE MINMAP FAKO

- CLEARANCE: SPECIAL FINANCE CONTROLLER – LIMBE CITY COUNCIL

-PAYMENT TREASURY: PAY MASTER GENERAL

-CONTRACTORS: TO BE SELECTED THROUGH THIS ONIT.

-OFFICIALS RESPONSIBLE FOR UNANNOUNCED CONTROLS OF THE EXECUTION: He shall carry out unannounced controls for the good execution of the works of this Contract as per their attributions. The role of the contractor shall be played by the selected enterprise.

CONTRACT MANAGER: CHIEF OF TECHNICAL SERVICE – CDO LIMBE III COUNCIL

###### Article 5: REPRESENTATION AND DOMICILIATION OF THE ENTREPRENEUR.

5.1- Within fifteen (15) days that follow the date of notification of the service order to begin works, the entrepreneur should designate the site foreman who will have the right of representation and sufficient decision to direct the site, to do the necessary supplies and to engage the enterprise.

5-2 - For the execution of the present Jobbing Order, the entrepreneur “elects domiciliation in Limbe ". In case of change of domiciliation without informing the administration, all notifications destined to the entrepreneur will be addressed to Limbe III Council notice board the place of execution of works.

Article 6: SERVICE ORDERS AND CORRESPONDENCES.

All Service orders of administrative natures and those with financial incidences shall be signed by the Contracting Authority and notified by the project owner or his/her representative. Service orders of technical natures shall be signed by the control engineer and notified by the project owner. The entrepreneur has ten (10) days within which he has to give observations on all service orders received. The fact of giving out some reservations does not free the enterprise from executing the service orders received.

##### CHAPTER II: EXECUTION OF WORKS

###### Article 7: KNOWLEDGE OF THE SITE AND GENERAL CONDITIONS OF WORKS

The entrepreneur shall visit the site at his/her expense to acquaint him/her with the effective work to be done and make concrete performance proposals. He is expected to have visited and acquainted himself with the site of works and the surroundings so as to have adequate knowledge of all its features, the nature of works to be executed, the importance of materials to be supplied, ways and means of access to the site, the necessary facilities, and also the following:

- The general conditions of execution of works and in particular the specific needs,

- The proper physical conditions of the work site (the nature of soil, the nature and quantity of materials met on the surface or likely to be met underground, etc),

- The local, normal and exceptional meteorological and seismic conditions: their consequences (water erosion, the possibilities of flooding and the position of the water table),

- The local conditions, particularly those of supplying and storage of the materials,

- 0The means of communication, transportation, and the supply of water and electricity,

- The possibility of sufficiently providing the qualified manpower,

- All constraints resulting from the social legislation, the fiscal and customs regime applicable to him,

- The possible presence of nearby enterprises also executing distinct contracts,

- The obligation to conform himself to the hygienic and security plans as well as to the yard regulation and to the staff's security and discipline.

In conclusion, he must obtain all information concerning the risks and the circumstances likely to influence the conditions of execution of works or their prices.

To this effect, he will not be able to take advantage of any mistake, omission or imprecision’s contained in the clauses of the Contract Notebook.

He will regularize if the case arises, the damages without intervention of the administration. The contractor shall be installed on the site by a Commission comprising of:

-The Mayor or his Representative	Chairperson

_The Divisional Delegate MINEE or her representative	Secretary

-The Chief of Technical Service (CDO - LIMBE III) Contract engineer	……. Member

- The Divisional Delegate of MINMAP or his representative	…….. Observer

-The entrepreneur	…….Member

Article 8: CONSISTENCY OF WORKS

The works, that form the subject of the present contract, consist of all works foreseen in the quantitative and bill of estimate.

Article 9: ROLE AND RESPONSIBILITY OF THE ENTREPRENEUR

The entrepreneur has as mission to assure the execution of works under the control of the control engineer and in accordance with the rules and norms in force.

The entrepreneur is responsible with regard to the administration, of the organization and the conduct of the site, of the quality of the materials and supplies used by him, of their perfect adaptation to the needs of the site and the good execution of works.

Works will be executed in accordance with the plans and technical specifications, according to the rules of art and according to the technical norms in force.

To this effect, the entrepreneur should take all measures to provide all necessary means and to hire the whole specialized staff.

The entrepreneur remains responsible for the totality of the site, including interventions of his/her accepted subcontractors. It is his/her responsibility to assure the coordination of the benefits of the suppliers, of the subcontractors whose contest is necessary to him for the different working corps on site, in due time their intervention under his/her direction and the good execution of the orders given by the control engineer.

Regular site meetings will be held at the initiative of the control engineer. The participation of the site foreman to site meetings will be obligatory. To this effect, the entrepreneur will keep a site register that will be available to the control engineer and his/her representatives.

Article 10: DURATION OF EXECUTION

The works foreseen in the present contract must be finished within four (04) month starting from the date of the notification by the control engineer to begin works.

###### Article 11: PROGRAM OF EXECUTION

Within ten days from the date of notification of the award of the contract, the entrepreneur will submit to the contract engineer the program of works in five copies for approval. The Mayor shall ONLY sign the contract when the approved program of execution is at his level.

The entrepreneur will constantly hold up to date the planning of works, considering the advancement of the site works. The important modifications brought to this program will only be applied after having received the control engineer's previous agreement.

It will be established every month end, at the entrepreneur's diligence and at his/her expenses, the state of advancement of works to be sent to the administration in seven copies.

Article 12: PLANS AND DOCUMENTS OF EXECUTION.

The plans of details and other necessary documents for the execution of works will be established by the contractor on the basis of the technical file.

Before the final reception, the contractor will hand to the control engineer three (03) copies of the plans of works really executed (plan de récollement) with one reproducible original.

Article 13: SUBCONTRACTING OF WORKS

All subcontracting to a third enterprise of the execution of a part of the works foreseen in the present Contract is subordinated to the prior authorization of the Delegated Contracting Authority.

Article 14: PENALTIES AND RESTRAINT OF DELAY

In case of delay on the duration of execution of works fixed by this present contract, the entrepreneur will be liable to lateness penalties whose rate corresponds to 1 /2000th of the amount of the Contract from the first to the thirtieth day of delay and 1

/1000th of the amount of the Contract for each day above 30 days of lateness. Where the total penalty amount exceeds 10% of the Contract amount, the Contract will be terminated Article

##### 15: RECEPTION OF WORKS

###### 15-1. Prior Operations to the Reception of Works.

Before the reception of works, the entrepreneur will request the control engineer by writing, for the organization of a visit to the site (technical acceptance of works executed). This

visit includes operations among others:

- The qualitative and quantitative knowledge of the works executed;

- The tests possibly foreseen by the STC/CCTP;

- The possible observation of the non-execution of the works foreseen in the contract;

- The relative observations to the completion of works;

- The observations of the quantities of works effectively executed.

These operations are the object of a written report signed by the control engineer and countersigned by the entrepreneur. At the end of this pre - reception visit, the control engineer may possibly specify the reserves raised and the corresponding works to be done before the date of reception that will be fixed by the Authorizing Officer.

###### 15-2 Provisional Reception of Works

The provisional reception commission will be composed of:

-The Mayor or Representative ………………………………………………………... Chairperson

_The Divisional Delegate MINEE Contract Engineer	Secretary

-The Chief of Technical Service (CDO) contract Manager	Member

- The Divisional Delegate of MINMAP or his representative………………………………………. Observer

- Store’s Accountant…………………………………………………………………………….. Member

-The entrepreneur	Member

This commission shall examine the report of the previous operation minutes to the reception and shall proceed to the reception of works if necessary. This will be the object of a reception report signed by all members in 07 copies (01) copy to the Divisional Delegate of Public Contracts - Fako) in the case where the works are executed completely following norms and in conformity with the technical plans.

###### 15-3 Final reception

The final reception will be pronounced by the same commission one (01) year after the provisional reception if all tests and tests of technical character give satisfaction.

The Contract won't be considered finally executed except on deliverance by the administration, of a final reception report.

###### Article 16: OBLIGATION OF THE ENTREPRENEUR

The entrepreneur is expected to have knowledge of the site and the conditions for the execution of the works which are the subject of this present Jobbing Order. He is held otherwise to fulfil his/her fiscal duties to the staff deployed for the execution of the works and should put in place an installation and an organization of the site guaranteeing the security of supplies and people on the site. He will be held responsible therefore for any damage that would occur on the material and people on the site because of his/her works until the end of the period of guarantee.

The entrepreneur is responsible with regard to the Mayor of the quality of the materials and supplies used their perfect adaptation to the needs of the site, and the good execution of works.

The entrepreneur will be held fully responsible for accidents and damage of all nature that would occur to his/her staff, third parties, agents of the control engineer, his/her material for the realization of the present contract, during the execution of the works.

He has the obligation to put back to original state the surrounding works damaged because of his/her works.

###### Article 17: INSURANCES

The entrepreneur should justify that he is a holder of a civil responsibility insurance policy, for the damage of all nature caused to a third party:

- By his/her salaried staff in activity;

- By the material that he uses;

- Because of the works.

Otherwise, the site should be covered concerning the works by a global site insurance delivered by a company recognized by the ministry in charge of finance. The inherent expenses to this insurance are the entrepreneur's load.

No payment with the exception of the advance of starting will be done without presentation of a certificate of a company proving that the entrepreneur fully regularizes the insurance premium or relative contributions to the works of this present Jobbing Order.

The entrepreneur has duration of fifteen (15) days from the date of the service order requesting him to begin works to present a certificate from an insurance company proving that he fully regularized the insurance premium or relative contributions to the works of this present Jobbing Order.

###### Article 18: DURATION OF GUARANTEE

The duration of guarantee for all works undertaken in this Contract is fixed at 4months (04) months, counting from the provisional reception date.

This duration will be prolonged until works have been put in state of final reception. Until the moment of this reception, the entrepreneur should assure the charge of all repairs or repairing whatever there are.

###### CHAPTER III - FINANCIAL PROVISIONS Article 19: THE AMOUNT OF THE CONTRACT

The Contract is a unit price contract. The amount of the Contract is closed at the sum of Sixteen million five hundred thousand (16,500,000) FCFA TTC.

The prices presented on the unit price slip are supposed to have been established on the basis of the economic conditions in force in the Republic of Cameroon.

###### Article 20: METHOD OF PAYMENT OF WORKS

Works will be paid on the basis of the deductions established by the control engineer in accordance with the real value of works executed and taken in to consideration for part payment by the control engineer.

###### Article 21: BANKING DOMICILIATION

The payments will be done through the General Treasurer of Buea to bank account N°	opened by the entrepreneur in the ……………………, Agency of	All banking domiciliation modification can only be effected by way of an additional clause.

###### Article 22: FINAL SECURITY BOND

The final security bond guaranteeing the complete execution of works will be constituted within twenty (20) days counting from the date of notification of the present Contract by the control engineer.

Its amount is fixed at 2% of the total amount all taxes included of this jobbing Order.

The final security bond can be replaced by a personal and interdependent guarantee by a first rate banking establishment installed in the Cameroonian territory and accepted by the Ministry in charge of Finance.

At completion of the corresponding amount for the contract, the security bond will be restored, or the banking guarantee of substitution freed on written request by the entrepreneur, after the provisional reception of works.

###### Article 23: GUARANTEE DEDUCTIONS

A deduction of 10% of the amount with all taxes will be done on every payment as guarantee of works, which will only be freed after the final reception that will take place within one year after the provisional reception of works.

###### Article 24: START OF ADVANCE

It may be granted to the entrepreneur on express request and after justification on his/her part, an advance for starting of works according to Decree N° 2018/366 of the 20/06/2018. Whose amount will be at most equal to twenty percent (20%) of the nominal amount of the Jobbing Order. This advance will be guaranteed at one hundred percent (100%) by a first rate banking establishment accepted by the Ministry in charge of Finance.

###### Article 25: FISCAL AND CUSTOMS REGIME

This present Contract is subjected to the fiscal and customs regime in force in the Republic of Cameroon.

###### Article 26: SECURITY

In application of the regime of public contract as security instituted by the decree N° 2018/366 of the 20/06/2018 are designated as follows:

- Person responsible for the liquidation of the Contract: The Mayor.

- The Treasury in charge of the payments: General Treasurer of Buea

- Competent civil servant to provide information enumerated with respect to the execution of this present Contract: the project owner.

###### Article 27: Stamp duty and registration of contracts (article 37 of GAC)

Thirteen (13) original copies of the Contract will be produced, (07) copies will be stamped and will be registered at the entrepreneur's expenses, in accordance with the regulation in force. The entrepreneur has duration of 15 days maximum from the date of signing of this present Contract to have already done its registration. After this dateline, the Contract can be liable to termination by right. After registration, the Contract should be returned on time prescribed by the competent service for distribution.

###### Article 28: PROVISION FOR PENALTIES

No to the state but yes to service provider

##### CHAPTER IV - VARIOUS PROVISIONS

###### Article 29: LITIGATIONS

All litigations occurring between the two parties in respect of the execution of this present Contract shall be the Subject of tentative reconciliation conciliation by direct understanding.

Failure to reach the out-of-court settlement, all differences ensuing from the Contract will be carried before the competent Cameroonian jurisdiction in accordance with decree N° 2018/366 of the 20/06/2018.

###### Article 30: CASE OF FORCE-MAJEURE

None of the parties will be considered to have failed in his/her contractual engagements so long as the execution of the works has not been delayed, hindered or prevented either by a cause of absolute necessity. Will be considered like cause of absolute necessity acts, situations or events escaping the control of the parties and presenting an unforeseeable and irresistible character.

The entrepreneur will see his/her responsibility freed only if he informs the administration of his/her intention by writing invoking this cause of absolute necessity and this/her, before the end of the tenth (10th) day after the event.

In any case, it is incumbent on the administration to appreciate the evoked causes of absolute necessity and the proofs provided by the entrepreneur.

###### Article 31: TERMINATION

This present Contract can be terminated as foreseen in Decree N° 2018/366 of the 20/06/2018 regulating public contracts.

###### Article 32 and last: VALIDITY

This present Contract will only become final after its signature by the Public Independent conciliator LIMBE III COUNCIL. It will enter in force from its notification to the entrepreneur by the control engineer.

Page and last of the Contract NO………/ ONIT/LIIIC/FAKO/L3C.TB/PIB2026

AWARDED AFTER OPEN NATIONAL INVITATION TO TENDER WITH The enterprise	B.P

…………………………………

#### FINANCING: PIB 2026 MINEE RECORD NO:

##### TECHNICAL SPECIFICATION AND DESCRIPTIVE NOTE

SPECIAL TECHNICAL SPECIFICATIONS

WORK DESCRIPTION

The purpose of this Open National Invitation to tender is FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

- Site:

- BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

GENERAL DESCRIPTION

CONTENTS

INTRODUCTION.

CHAPTER I: 	GENERAL INFORMATION……………………………

Article 1:  Subject……………………………………………………….

Article 2:  Role of the Contractor …….………..

Article 3:  Work plan ………….....

Article 4:  Site selection and choice of Drilling Technique.…………………

CHAPTER  II :	DRILLING WORKS

Article 5 : Drilling of Borehole………………….........................................

Article 6 : Guarantee of works .................................................................

Article 7 : Origin and quality of material and equipment......

CHAPTER  III:	SUPPLY AND INSTALLATION OF EMERGE MANUAL PUMP.

Article 8:  Supply-Installation of a Manual pump……………………….......

Article 9 : Transport, Delivery and installation of ………………………….

Article 10 :  Provisional Reception………………….........................................

Article 11 :  Conditions for the Final Reception …….......................................

CHAPTER IV: 	ORIGIN AND QUALITY OF GEOMATERIALS AND CEMENT

Article 12: Quality and Quantity of Geo-materials

Article 13: Origin and quality of sand

Article 14: Origin and quality of gravel

Article 15: Origin and quality of stones

Article 16: Origin and quality of cement

CHAPTER V:	 METHOD OF EXECUTION

Article 18: General Information

18.1: Security at the work site

18.2: Traffic

Article 19: Stone Masonry

Article 20: Pointing and plastering

20.1 Pointing

20.2 Plastering

Article 21: Plumbing works

21.1 Pipe Specifications

21.1.1 Control tests on pipes

21.2 Fitting specifications

Article 22: Piping

22.1 Description

22.2 Care/Laying of pipes

22.3 Methods of determining quality of G.I and PVC piping laid.

CHAPTER VI: CONSTRUCTION METHODS

Article 23: Setting out of Works

Article 24: Excavation of Trench

Article 25: Backfill

INTRODUCTION

This specification aims to define the mode of execution of work to be done following the norms and approved standards, according to the documents of the Jobbing Order.

The choice of technological options for achieving the proposed work has the sole concern to ensure a better functionality of facilities in compliance with safety rules for the protection of property and persons.

It has been established as a guide to clarify and supplement the guidance of the estimate and drawings notwithstanding the terms of the Jobbing Order.

The technical specifications presented herein below define the hydro-geological waterworks and electromechanical engineering works that shall be executed  in BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY in Limbe III in Fako Division and the manner in which these work shall be carried out. So the Contractor is expected to read these specifications critically and identify all the articles that are applicable to his job.

CHAPTER I: GENERAL INFORMATION.

Article 1: Subject

The following Technical Specifications Journal (TSJ) concern the works to be carried out in the construction of 3 (three) boreholes, the supply and installation of 03 (three) manual pumps in the boreholes and the construction of the superstructure  in BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY - Limbe III in Fako Division; as well as the setting up of measures to sustain the equipped borehole.

In each case, the volume of work to be executed is indicated by the bill of quantities, network map and/or plan provided for the project. The various works to be executed shall conform to the relevant terms of the technical specifications given herein below.

Article 2: Contractor’s role

The Contractor who shall be chosen after this call for tender, shall be responsible to execute the works. These include all the phases from site selection, through the drilling of the borehole, the borehole design, the cleaning and development of the borehole, the determination of the properties of the aquifer (Aquifer or Pumping test) and the superstructure construction, to the pump installation, water analysis and the taking of long-lasting measures to ensure the project sustainability.

It should be understood that the provision of a bill of quantities for any project does not absolve the potential Contractor of the necessity to affect a well-planned site visit, at his own expense, to gain complete knowledge of the conditions prevailing on the terrain. This knowledge shall come in handy when preparing the List of Tasks and the Unit Price Schedule. Potential Contractors (or Bidders) shall provide a detailed and sequenced List of Tasks to be effected on each component of the project. Within fifteen (15) days from the date of notification to start work, the Contractor shall provide the Supervising Engineer with:

-A detailed plan of the work, showing the scheduling of the various works to be executed in time

-Detailed technical drawing of the works to be realized

-A manpower deployment plan

-A schedule of the delivery of materials to the project site, showing possible delays

-Failure to forward the foregoing documents shall engender the postponement of the reception of project materials, which could result in a punishable overall delay in the execution of the project.

No material shall be used that has not been checked for conformity with the technical specifications by the Supervising Engineer.

The Supervising Engineer reserves the right to modify the plans and Work schedule provided by the Contractor, which modification shall first be submitted to the Delegated Contracting Authority for approval. Under exceptional circumstances, the Supervising Engineer may suggest modifications to the technical specifications for any component of a project to the Delegated Contracting Authority, while making sure that the overall cost of the project stays within the limits of the financial bid of the Contractor.

Any modification must be done in writing, with sufficient justification. For this purpose, a numbered page book (the project log book) shall be kept on site in which the Supervising Engineer shall write his approved instructions. Both the Contractor, or his representative, and the Supervising Engineer shall initial every page of the project logbook

It is therefore obligatory for the Contractor to execute the works in conformity with:

-The Bills of Quantities and Estimates,

-The Special Administrative Clauses

-The Special Technical Clauses stated herein,

-Any other special rules and regulations that may be applicable to his job,

-The work schedule,

-The detailed technical drawings,

Subject to any approved modifications indicated in the project log book by the Supervising Engineer,

the Contractor shall take note of any omission or discrepancies that may exist in the three documents mentioned in the preceding paragraph, which omission or discrepancies could fundamentally affect the technical or aesthetic quality of the works executed to his detriment, and call the attention of the Supervisory Engineer who shall remain at his disposal of the Contractor for necessary information and inquiries through the duration of the project.

In this regard, the Contractor shall not absolve himself of the responsibility for poor quality work by citing imprecision, omissions or discrepancies in the technical specifications or modifications thereof indicated in the project log book by the Supervising Engineer.

Any works effected without regard for the foregoing instructions or provisions shall be demolished at the expense of the Contractor

Article 3 - Work plan

The Contractor shall execute the work within a deadline of three (03) months as from the date of notification of the service order to start work.

Article 4 - Site selection and choice of Drilling Technique

4.1-   Site Selection :

The site for the borehole shall be chosen after hydrogeological and geophysical studies. These studies will start with the interpretation of aerial photos of the area aimed at locating fractures and structural traps to retent aquifers. Geophysical prospecting will then be carried out on these anomalies so as to confirm the hydrogeological results and obtain precisions on the aquifers. This geophysical surveys will be done using the Electric Method, precisely  Resistivity Profiling and Resistivity Depth Sounding.

Studies carried out on previous boreholes done in similar geological formations show that with the respect of minimum precautions during site selection, a success rate of ……% (minimum yield of 0,7m³/h after designing the borehole) is expected.

The selected site will therefore depend on the results obtained after these surveys ; but the ideal site will be that which will be easily accessible to the beneficiaries. A site selection report shall be presented indicating the methods used in choosing the site and also outlined in a sketched plan of location.

4.2- Choice of Drilling Technique:

The hydrogeologic nature of the area is such that drilling will be done in unconsolidated and hard formations and consequently requiring the use of a well-equipped drilling rig in order to face any eventuality.

The borehole facilitates the extraction of water from deep aquifers in fractured hard rocks, thereby making it possible to prevent pollution from superficial waters. Precautions are therefore taken to isolate superficial formations so as to avoid the vertical downward propagation of superficial pollution.

Drilling through the loose formations may need the use of a drilling fluid which can be water or muddy water; and of course the temporal use of PVC or metallic casing of diameter 175-195mm .

Drilling shall be done using compressed air supplied by a high pressure compressor. The tool and bit, used should be adapted both to the loose and hardrock formations.

Studies on existent boreholes in the area reveal that the depth will be between 40m and 80m (averagely 60m) therefore the drill pipes or rods should be available to attain this depth.

The superstructure shall be of the classic type: a pump stand on a slightly inclined margelle with a ditch at the edges that lead to a drainage system which ends up in a soak away pit at a distance of at least 8m away from the borehole.

The borehole shall be equipped with a manual pump of the type SWN 80 or India mark II or Vergnet. The bodywork of the pump and  its accessories should be composed of materials that are resistant to corrosive water and cannot be oxidised.

CHAPTER II – DRILLING WORKS

Article 5 - Drilling of Borehole

The borehole shall be drilled respecting the technical specifications outlined here and shall be accepted  as productive (positive) if its yield is at least 0,7 m³/h (700l/h) and the water is potable after analysis.

5.1. Organization of the work-site

Considering the results obtained after previous drilling campaigns of boreholes in the area, an average depth of sixty (60)m is proposed for the borehole.

The success of this project largely depends on the perfect coordination of the different activities by the Contractor (the Supply and the installation of the manual pump, the drilling process respecting the appropriate drilling technics, the appropriate borehole design, cleaning and development of the borehole, the pumping test, the construction of the superstructure with a good drainage system, water analyses, project sustainability). This coordination requires the strict respect of the execution plan of the borehole which contains the outlined execution plans of the different activities.

The Enterprise shall place its Technical Director who shall be responsible to the Administration and on the worksite, the work execution shall be supervised by a Foreman who is well qualified and experienced in the domain of borehole drilling, manual pump installation and project sustainability. The execution plan should be conceived in such a way that the different phases will be done without unjustified stoppage.

The state of work progression shall be established monthly and if after two months, the progression rate is considered low, the Contractor shall be asked to deploy additional means to the worksite so as to accelerate work progression and meet up with the deadline.

During the work execution, the Administration has the right to modify the work.

5.2. Working Hours.

The general conditions fixed for workers by the Cameroon Legislation also applies to the Contractor’s workers in the worksite. There shall be no work at night.

5.3. Equipment and Materials for execution

5.3.1 General conception of equipment and materials

The Contractor shall be responsible for the choice of the equipments and materials. The general conception of the drilling rig and the materials to be used for the execution of the borehole should take into consideration the local milieu : the state of roads and accessibility, as well as the rate of execution stated above.

5.3.2. State of the equipments and materials

The execution calendar obliges the Contractor to be in possession of a drilling rig inorder to execute this project, immediately he is notified of having been chosen to execute the job.

The serial number, the age and the origin of the drill ought to be specified in the bid. Anyway, the proposed equipment should be in a good state.

5.3.3. Description and specifications of the drilling rig.

The drilling rig that is needed for this project will be composed of:

The Drill

A conventional  rotary apparatus using compressed air and water or mud, and specially adapted to using the tool and bit in loose formations and the down-the-hole hammer in hardrocks. Drilling through the loose formations and to avoid frequent collapse of these formations especially when the hardrock is to be drilled, the use of temporal casing is very obligatory. This temporal casing can be of steel or PVC nature and facilitates drilling in both the loose and hardrock formations without any difficulty.

The drilling rig should have a capacity of attaining an average depth of 100meters with a borehole diameter of:

12¼" (175-195mm) for rotary drilling with compressed air using  tools and bits with water or mud,

6¼" (165mm) for rotary destructive drilling with compressed air by using the down-the-hole hammer.

Other Equipments.

The Air Compressor :

This should be a high pressure compressor of air, of at least 5 m3/mn at 7 bars.

Sufficient Steel pipes, attaining an average deth of 100m.

Pumping tests should be done using an immerged manual pump of diameter less than 110mm,  and capable of supplying yields of 10 m³/h at a depth of 30meters and of 6 m3/h at a depth of 80meters.

An Electric sounder for the measurements of the water levels in the borehole ought to be available.

Each drilling team should have a rapid means of communication.

5.3.4   The Conformity Visit.

A conformity visit of all the equipments and materials shall be done at the beginning of the work execution inorder to verify:

their conformity with those proposed in the Contractor’s bid,

the relationship between the capacities of  these equipments and  materials, the      prescriptions in the Technical Specifications Journal and the execution period.

The pronouncement of this visit shall be expressed in a Report which shall not in any way set free the Contractor from his engagements.

5.4. Description of the Borehole.

5.4.1 The Method of execution of the Borehole.

The choice of the methods and materials to be used as well as the exact diameters of the borehole would be at the initiative of the Contractor and under his sole responsibility.

The following  specifications have been  tentatively presented . Anyway, it is specified that:

except by special derogation, drilling with the down-the-hole hammer in the hard bedrock shall never be done without the use of the temporal PVC or steel casing, at the levels of the loose or unconsolidated weathered formations,

the drilling through the loose nonconsolidated sections of the weathered rocks may require the use of water or muddy water or mud. The substances used should  have a composition that would not seal the productive layers and should be biodegradable.

5.4.2 Sampling.

During drilling, the samples of the cuttings shall be taken at every change of faciès (rock type) or every meter. The samples shall be placed in small labelled (depth of sample) plastic bags and kept in the worksite at the disposal of the Contract Engineer, who shall decide on their outcome.

5.4.3 Characteristics of the Borehole.

The principal characteristics of the borehole are summarized as follows:

Borehole in the hard bedrock:

Drilling in the loose unconsolidated weathered rock formations by rotary drlling of minimum diameter 9"5/8 right to the contact with the hard bedrock,

Putting in place of a column of temporal casing of diameter 178/195mm  in PVC or in steel,

Continuous drilling in the hard bedrock using the down-the-hole hammer, of diameter 165mm, right to a maximum total depth of 100meters,

Putting in place of a catchment colon using the  PVC Screen of diameter 110 – 125mm with slot openings of  Ø ≤ 2mm,

Putting in place of a gravel pack of a quartzeous nature and calibrated: (1 - 2mm) or (2-4mm),

Putting in place of a seal composed of alluvium or elluvium,

Withdrawal of the temporal Casing,

Putting in place of a concrete borehole cap of 2m minimum.

5.5. Borehole Design

If the borehole is considered exploitable, its design is carried out immediately the drilling process comes to an end.

In all the cases, the productive borehole shall be designed all through the length of the catchment zone  PVC casing of diameter110/125 mm, of which the characteristics are specified further below in this file.

This casing shall be armed with slot openings of Ø ≤ 2mm (Screen), which shall be placed  at the levels of water arrivals by screen fragments of length 3 or 6meters. The base of the colon shall be blocked with borehole stopper.

The annular space between the soil formation  and the PVC colon shall be filled with a quartz gravel pack of a grain-size: (1 - 2mm) or (2-4mm) all along the length of the screen plus 3meters. The gravel shall be disinfected being introduced into the annular space of the borehole.

The grain size of the gravel shall be 1-3mm. The gravel shall be composed of  clean quartzeous and smooth material.

On top of the gravel pack filter, a clayey seal of 1meter thick shall be put in place, it has as goal to prevent the pollution of the borehole by superficial waters.

Above the clayey seal, the borehole shall be filled  with alluvium or elluvium , in which case this substance shall constitute material for effective back-fill, and finally the top of the borehole shall be filled with concrete for a depth of 2meters.

The casing shall overlap the earth surface by 0,50m. This casing shall be momentarily locked    with a screwed cork.

5.6. Development

Development is done by air-lift with double tube using the drilling rig or an independent unit.

The yield obtained after the development should not be more than 10 % less than the yield obtained at the end of drilling.

Development shall continue until clean water with no residual sand grains nor clay particles is observed. The Contractor should control the yield in sand grains of the water, by applying the Method of observing sand deposit in a10litre bucket of water and of which the diameter should not be greater than 1cm at the end of development.

The average time for development shall be 4 hours.

If technical errors occur during the drilling process or during development, the additional time beyond the 4hours, shall be under the responsibility of the Contractor and, if clean water is not obtained after development, the borehole will not be received.

In case an independent unit was used for development, the return of the drilling rig for the partial or complete repeat of the drilling process, shall be under the charge of the Contractor.

The yield shall be measured after every 15 minutes. The water level and the depth of the borehole shall be measured before and after the development.

The accepted  tolerance for the measurements  (including those obtained during pumping test) shall be :

-	10% for the yields,

-	1cm for the water level,

-	5cm for the measurements of depth.

5.7. Pumping [Aquifer] Tests-Superstructures-Disinfection of the Borehole and Water Analyses.

5.7.1 Pumping [Aquifer]Test.

These tests shall be executed using an immerged pump, of a minimal capacity of 10 m3/h at a depth of  30m or 6 m3/h at 80meters. The pumping test (type CIEH) shall be done for a time lapse of 4 hours (3 phases of an increasing yield). The processes shall comprise : Restoration, Pumping and Recharge. The recharge after pumping shall be done for an hour. The mesurements of the water levels shall be effectuated using an electric sounder,  while the measurements of the yield shall be done using 200litres drums. All the measurements shall be recorded in forms recommended by the Ministry incharge of Water.

5.7.2 Superstructures

The Contractor shall have to construct the following superstructures:

A reinforced concrete corping of dimensions 1.5m x 1.5m and of height  (20cm) which is compatible with the manual pump, and situated above the reinforced concrete slab,

A reinforced concrete slab of minimum size 2m x 2m surrounding the reinforced concrete corping, raised above the soil surface of minimum height 15cm and and slightly inclined with a gentle slope of about 2% towards the evacuation outlet.

A ditch surounding the slightly inclined reinforced concrete slab to drain water from the latter to the outlet, through the buried PVC pipes of minimum length 8m, into the soakaway pit. The soakaway pit shall have a dimension of 1m x 1m x 1m and filled with stones ; and shall be covered by a concrete slab of thickness 10cm.

A protective layer against erosion of width 1meter all round the half wall and composed of lateritic gravel of thickness 10cm, shall be put all round the half wall.

A model plan shall be available. The superstructures would, however, be constructed on the

basis of detailed plans that are convenient for the type of manual pump which shall be

accepted by the Contract Engineer. The bidder ought to enclose these detailed plans in his bid.

The concrete ought to have a composition of 350kg of cement per m3 and after 28 days have a resistance of 28 kN/cm², it shall be reinforced with welded iron rods forming a grid of 150mm (diameter of the rods being 6mm). Provision must be made for clean aggregate, gravel and sand, as well as non corrosive water.

The set-up shall be completed by the construction of:

A half-wall surrounding the ditch of dimension : l=3m, w=3m and h=1,2m; which shall be painted with oil paint or covered with tiles. It shall have an entrance which shall be equipped with a metallic gate of height 1,2m and width 1m. This gate shall be painted with a different color from that on the half-wall.

The drainage system: a plughole or drain (with a grid capable of retaining solid particles) that leads to a concrete sewer manhole (0,5mx0,5mx0,5m) where resistant solid matter settles; and water flows into a buried PVC pipe of Ø for a distance of at least 8m and then empties itself into a soakaway pit of dimension 1m x 1m x 1m  (completely filled with stones). This soakaway pit shall have a concrete slab as cover of thickness 10cm.

The identification number of the borehole and the date of execution shall be carefully engraved on a non oxidizing  metallic plate permanently pasted on the concrete of the pump support; and on this plate shall also be indicated the origin of the funding.

5.7.3 Water Analysis.

Before the borehole design, the Contractor shall carry out the following measurements: pH, conductivity, temperature.

At the end of Development, the Contractor shall proceed to the disinfection of the borehole by the injection of Calcium hypochlorite (or its equivalent) into it.

At the end of the Pumping test, the Contractor shall proceed to the sampling of water to carry out physico-chemical analyses that shall be done in Laboratories recognized by the Administration.

5.8. Control of the Works.

The supervision and control of the works shall be done by a Controller or a Consulting Firm under the coordination of the Contract Engineer.

5.8.1 Worksite logbook.

Inorder to carry out an effective follow-up of the execution of the project, the Contractor shall make available in the worksite a logbook on which shall be recorded everything concerning work progression. This log book will help the Controler, on arrival in the worksite, to exactly know the state of evolution of the project.

The book will be held by the "Recorder",  an employee of the Enterprise, and that will be his sole task in the worksite. The Recorder shall always put in writing all the daily activities in this book, as operations evolve.

In this book shall be recorded the following informations:

Name of worksite (name of village),

Serial number of borehole in the village,

Dates and time of arrival and of departure of the drilling rig,

Time used to run the compressor to execute the borehole,

Time used in installing the drilling rig and time that drilling started,

Drilling time for every pipe,

Diameter and method used in sinking every pipe,

Depth attained by every pipe,

Nature of rock formations cut through "driller’s cross-section",

Depth of temporal casing, time used in placing and removing the temporal casing,

Composition of the borehole design : length of casing, screen, volume of gravel pack, level of the emplacement of the clayey seal, thickness of the concrete, etc.

Duration and yields of pumping test, water quality and levels following the instructions given by the  Engineer during the Development and Pumping test operations,

In short, all the technical details, incidents, breakdowns, difficulties specific to the evolution of the project, indicating the time these occurred.

The book shall be signed by the Representatives of the Administration and that of the Contractor, and shall serve as the basis for the establissement of vouchers.

Remarks and reserves made by the Contractor and/or the Administration shall be recorded in this book.

5.8.2 Control and supervision

The control and supervision of works shall be carried out by the Divisional Delegate of Water and Energy or his representative and shall be based on the following items:

Definition of the work plan and its execution calendar in agreement with the Contractor.

Site implantation (setting out).

Indicative forecasts on the geology and on the depth to be attained by the borehole.

Decisions on whether to continue or stop drilling, its design or its abandonment.

Elaboration of the borehole design in collaboration with the Chief driller, taking into consideration the yield.

Supervision and interpretation of  the Development and Pumping test results.

Choice of the configuration of the superstructures depending on the landscape (topography).

Supervision of the pump installation and the training of local pump caretakers.

Supervision of the analyses related to water quality.

Control the effectiveness of the activities concerning the training and sensitization of the Water Management Committee.

5.9. Origin and quality of materials

5.9.1 General dispositions.

The Contractor shall present to the Delegation incharge of Water Resources for approval the materials he intends using, indicating their nature and their origin. All the materials found faulty shall be evacuated by the Contractor at his own expenses. The Contractor shall be responsible for the regular supply of materials  for the smooth running of the project.

Not withstanding the approval of the quality and origin of the materials by the Delegation incharge of Water Resources, the Contractor remains solely responsible for the quality of the materials used for the project. It is left for him to carry out at his own expenses all the necessary tests and analyses to be sure of the materials used.

It is left for him to make all the necessary moves to obtain autorisations or permissions, and carry out payments if necessary to enable him exploit quarries or other substances, and the site for the installation of the project.

5.9.2 Characteristics of the casing and screen.

The casing and screen shall be of strong PVC (types for boreholes). The diameters shall be 110/125 mm. The origin and  quality of these tubes ought to be approved before being used.

These tubes should be smooth, with solid round or square centralized fittings that can enable the tubes attain a depth of 100meters.

The tubes should have the garanti of being resistant to all the stress manipulations during their installation and during pumping. The PVC shall be composed of matter that cannot dissolve in water and modify its quality.

The slot openings of the screen shall be done mechanically in the manufacturer’s factory. The slot openings shall have a diameter of less than 1mm. The percentage of openings shall not be less than 2% of the total surface area of the PVC tube.

5.9.3 Cement

The cement to be used shall of the type PORTLAND artificiel CPA 325. It should be obtained in bags of 50kg. Any bag with hardened fragments shall be rejected. The recuperation of cement dust that has fallen on the ground shall be prohibited.

5.9.4 Gravel

The gravel introduced into the annular space of the borehole shall be clean gravel composed of smooth quartz and of grain-size 1-3mm.

5.10. Technical File.

A technical file of the borehole shall be prepared by the Contractor. This technical file shall contain:

the location of the borehole on the plan of the village,

the technico-geological cross-section of the  borehole,

the results of the Development and cleaning test,

the interpretation graphs of the Pumping tests indicating the depth of pump installation.

Article 6 : Guarantee of works

The Contractor shall take an engagement to execute the borehole with the materials he proposes and to respect all the technical norms in force.

In case of an accident leading to the abandonment of the borehole, le Contractor may be compeled to another borehole near the previous site, except the geologic conditions are abnormally unfavorable. The Contractor shall not be entitled to any remuneration for the abandoned borehole.

The obligations of the Contractor during the guarantee period consist of changing, or reparing the worn out parts or those that have been damaged due an error by the manufacturer.

Article 7 - Origin and quality of materials and equipment

The Contractor shall present the materials and equipments he intends to use, with indications of their nature and origin, to the Contracting Officer, for approval. Any material or equipment that is found faulty shall be rejected and  evacuated by the Contractor and at his sole expenses.

Not withstanding the approval of the quality and origin of the materials by the Contracting Officer, the Contractor remains solely responsible for the quality of the materials used for the project. It is left for him to carry out at his own expenses all the necessary tests and analyses to be sure of the materials used. It is left for him to make all the necessary moves to obtain autorisations or permissions, and carry out payments if necessary to enable him exploit quarries or other substances, and the site for the installation of the project.

CHAPTER III - SUPPLY AND INSTALLATION OF EMERGE MANUAL PUMP

Article 8 - Supply-Installation of an three emerge manual pump

Characteristics of the manual pump

The choice of the pump shall take into consideration the government policy on the standards of hydraulic equipements for the rural communities. But the minimum characteristics of the pump shall : HMA=70 m, HMR=100 m Q=5m3

8.1 .Diameter

The borehole shall be equipped with PVC tubes of which the usable minimum internal diameter shall be 110mm.

8.2 Yield

The dynamic levels in the project zone shall be situated at an average depth of around twenty meters, anyhow the proposed model of pump shall be one that have to function without the dispensation of too much effort for installation depths of about 50m and of dynamic levels of equivalent depths.

8.3 Resistance to corrosion

All the parts constituting the pump ought to be resistant to water and air corrosion (in this case, the Contractor is asked to present documents to ascertain that control tests were carried out in the factory on  the supplied materiels or their equivalents to be supplied). The Contractor shall attach to his bid the list of parts that shall be in contact with water and specify their component elements and the anti-corrosion process to be applied on them.

8.4 Fittings.

The supply of the manual pump should also include:

the supply of tools to fix the pump onto the base: wire mesh welded with bolts, nuts and fitting washers;

the supply of seals.

The fittings that shall be used should have closing plates which should be put in place while waiting for the pump to be installed. All fittings shall be approved by the Supervising Engineer before use. The performance guarantee of work shall cover all defects in fittings, their handling and workmanship.

8.5 Maintenance

The Supplier shall fill a table describing the nature of the day-to-day maintenance operations   with as information for each case:

the periodic interval

the parts concerned

the costs of the parts in the locality

the required set of tools

8.6 Repair works

The Supplier shall specify the breakdowns that shall require the withdrawal of the pump from the borehole as well as the different unit weights, notably:

the whole fountain,

the linear meter of the aspiration pipe (with the rod) with and without water,

the pump cylinder.

For more frequent interventions, he shall specify the nature of intervention and its frequency.

8.7 Accessories

The Contractor should show the pump caretaker the  key or keys required to help  mount,  dismount and replace parts that have brokendown.

8.8 Spare parts

The spareparts ought to be, as from the beginning of the project, be available in the different sales points. A kit of spare parts shall be made available and handed to the Village Water Management Committee.

8.9 Technical and pedagogic brochures

The Contractor ought to make available technical and pedagogic brochures on the mounting, the good functionning, the maintenance and the repairs of the pump.

These brochures shall simultaneously contain three levels of information.

a) A level that exclusively illustrates the following themes:

How to pump correctly (illustrations with photos or drawings).

How to detect an abnormaly in the fonctionning of the pump.

How to carry out minor repair works.

b) A level that gives complete informations on the assembling of the pump for use and for maintenance. All the possible types of breakdowns that can occur should be mentionned as well as the means to remedy the situation.

c) A complete documentary level about all the aspects of the pump: manufacture, constituent parts, materials used, assembling, current maintenance, important repair works, list of the spare parts and their approximate lifespan, etc.

These brochures shall be delivered with the pump, a copy shall be kept with the Supplier’s representative.

Besides, the Contractor should prepare a maintenance form for the pump (as well as extra copies), which shall be kept in the village, and in which all repairs and maintenance works shall be recorded.

8.10 Putting in place of the maintenance system

The Contractor shall take care of the training of two (02) to three (03) pump repairers to carry out minor maintenance and repair works on the installed pump. The training of these pump repairers shall be a condition for the provisional reception of the borehole.

Article 9 : Transport, Delivery and installation of pump

The Contractor shall equally take care of the transportation and installation of the pump on the site.

Article 10 : Provisional Acceptance

The materiels to be used ought to undergo a qualitative provisional acceptance, which shall be based on the administrative and technical documents justifying  the quality of the materials used are in conformity with the technical objectives.

This reception shall be later followed by a technical acceptance which shall take place in the worksite  after the installation of the pump and after observing it functioning.

The decision taken during this acceptance does not liberate the Contractor from his engagements with respect to the deadline as well as the technical specifications.

Any change of material that was proposed in the bid (type, characteristics, origin, etc.) before or after the conformity visit and during the execution of the project, is forbidden except authorized in writing by the Contracting Authority, following the application forwarded by the   Contractor.

If the works are not in conformity with the specifications, the Contracting Authority can reject them and ask for their remplacement or necessary modifications, without any extra charge for this.

Article 11: Conditions for the Final acceptance

The final acceptance shall be pronounced after the expiration of the guarantee date which comes one year after the provisional acceptance. There shall be no specific pumping test during the final reception, but a test of the equipments used in exploiting the groundwater and a survey among the population to confirm the good working order of the pump during the one year guarantee period.

CHAPTER IV: ORIGIN AND QUALITY OF GEOMATERIALS AND CEMENT.

Article 12: Quality and Quantity of Geomaterials.

The Contractor shall supply all the sand, stones and gravel that may be required for the execution of any component of a project. He shall also be responsible for the excavation and backfilling of the pipeline under the supervision of the Engineer. In that regard, it is obligatory for the potential Contractor (or bidder) to visit the project site, at his own expense, before preparing his bids, in order to verify whether available geo-material are of good quality and of sufficient quantity. He shall make any reservations concerning geo-materials in his bid (Site Visit Report).

Article 13: Origin and Quality of Sand

The nature and origin of sand remain subject to the approval of the Supervising Engineer.  Sand shall be obtained either from rivers or through crushing of rocks. The sand shall be of high quality. It shall be crunchy, stable, and clean and shall be free of dust particles, schistose, gypseous or clayey debris and organic matter. It shall contain neither sulphur compounds no substances that can react with cement or metallic reinforcements. The sand component shall be more than 80% and the very fine constituents, with a dimension not exceeding eighty (80) microns that can be eliminated by settling, should be less than four percent (4%). No grain of sand should have a dimension greater than four (4) millimeters. If deemed necessary by the Supervising Engineer, the sand shall be sieved and washed thoroughly before use.

Moreover, filter grade sand shall have a grain size ranging from 0.8mm to 1.2mm inclusive. Furthermore, it shall be fried in order to eliminate algae zygospores, bacteria and/or bacteria spores, fungi and/or fungal hyphae.

Article 14: Origin and Quality of Gravel.

Gravel shall be obtained from deposits or quarries chosen by the contractor and approved by the Supervising Engineer. It shall be clean, without an excess of flat elongated pieces, dust or impurities. Constituents that can be eliminated through settling should be less than 2%.Its grading should be suited to its use. If deemed necessary by the Supervising Engineer, it shall be washed before use.

Article 15: Origin and Quality of Stones

Stones shall be obtained from deposits or quarries chosen by the Contractor and approved by the Supervising Engineer. No stone shall have a dimension less than twenty (20) centimeters. Basalts stones, commonly called black stones, are highly recommended, or else stones of other quality, such as un-weathered  granites, rhyolites, ignimbrites, etc, duly tested and approved by the Supervising Engineer may also be used.

Article 16: Origin and Quality of Cement

Cement shall be of the CPA 325 class and shall be obtained from an approved factory.

CHAPTER V: METHOD OF EXECUTION

Article 18: General Information

18.1 Security at the Work Site

The Contractor shall place at the entrance to work site signboards in bold letters indicating that work is underway and prohibiting the public and unauthorized persons from entering the work site. He shall be responsible for any accident that may occur on the work site or may be suffered by a third party, his staff and employees or officials of the Administration as a result of their presence on the work site. Organization of work and security on the work site shall therefore be the sole responsibility of the Contractor. Furthermore, the Contractor shall be bound by the labour legislation in Cameroon vis-a vis his workers and the Administration. Moreover, his insurance policy shall cover any damages he could cause to any one during the execution of the job.

18.2 Traffic

The Contractor shall be responsible for ensuring that traffic is not obstructed on the entire stretch of his work site throughout the period of work, right up till provisional reception. No obstruction of traffic shall be allowed for more than two hours. Maintenance of traffic flow shall be the responsibility of the Contractor. In case of any breach of contract in this matter , the Supervising Engineer may bring in a third party to correct any shortcomings that may be impeding the traffic flow, and related expenses shall be borne by the Contractor.

Where interference of the traffic flow for a given period is inevitable, the Supervising Engineer shall be informed of the situation at least 7 days in advance, so that he can seek the opinion of local Administrative authorities and get everything arranged beforehand.

In case a deviation has to be used, the contractor shall submit to the Supervising Engineer for approval after consultation with local administrative authorities, the deviation route and his plan for maintaining the deviation throughout the duration of the works that have necessitated the deviation.

Article 19: Stone Masonry

Stone masonry shall be aesthetical and in accordance with structure type and civil engineering rules. Binding mortar shall be a mixture of 400kg of cement per m³ of sand, no grain of which shall have a dimension exceeding 4mm.

Mortar containing a mixture of 450kg of cement per m³ of sand shall be used for the finishing of the external joints of non-visible walls of stone masonry

Mortar consisting of a mixture of 500kg  of cement per m³ of sand, to which shall be added a quantity of SIKA Nº 1 recommended by the manufacturer and approved by the Supervising Engineer, shall be used for waterproofing the interior  surfaces of water-retaining structures (storage tanks, interruption chambers, sedimentation basin, filters, etc).

Article 20: Pointing and Plastering

20.1 Pointing

The joints of all external walls of stone masonry that are visible shall be carefully pointed to give them an aesthetic look. Mortar containing 600kg of cement per m³ of sand shall be used for pointing with a cement paste (1:0) finish

20.2 Plastering

Plastering of surfaces in contact with water shall comprise pointing of the mortar joints followed by a 1cm thick layer of spatter dash 1:2 (m625). This shall then be followed by the application of a rendering coat of 2cm thick 1:4 (m300) mixtures and a setting coat 2cm thick 1:2 (m625).The walls shall then be finished with cement paste. Plastering of surfaces not in contact with water, such as chambers for air valves, control valves and washouts shall consist of 1 coat of plaster 1cm thick and a mixture of 1:3 (m400)

# II. SPECIFIC ENVIRONMENTAL AND SOCIAL CLAUSES

## Information and accompanying measures

The contractor shall, in conjunction with the Engineer, ensure strict compliance with the following guidelines the following guidelines:

- Carry out a communication and awareness campaign prior to the work on the work schedule of work, service interruptions and traffic detours, as required;

- Limit construction activities at night. If necessary, ensure that night work is carefully planned and carefully planned and that the community is informed so that it can take the necessary can take the necessary measures;

- Signpost the work;

- Conduct STI/HIV/AIDS awareness campaigns for workers and local populations.

- Prohibit: (i) cutting down trees for any reason outside the approved construction zone (ii) hunting or capturing local wildlife; (iii) using unapproved toxic products, such as products, such as lead paint; (iv) disturbing anything of architectural or historical value historical value;

- The community will be notified at least five days in advance of any service interruption (water, (water, electricity, telephone), through the press (giving priority to community or local radio stations where they exist).

## Site installations

The Contractor will propose the location of his site installations to the Contractor before the start of the works and will request authorisation to install them by means of a verbal note (as evidenced by the site report).

The site must be chosen outside sensitive areas, in order to limit the clearing of undergrowth, the uprooting of shrubs and the felling of trees. In the site installation area, trees with a diameter greater than 20 cm measured at 1 m from the ground may be pruned and felled with the prior agreement of the contract engineer.

The site must provide adequate water drainage over its entire surface area. Maintenance must be concreted and include a sump for collecting oils and grease. and grease. These maintenance areas should slope towards a sump created for the purpose and towards the inside of the platform in order to prevent the accumulation of water. towards the inside of the platform to prevent pollutants from running off into the unpaved ground.

At the end of the work, the contractor will carry out all the work required to restore the site.

The contractor must remove all equipment, machinery and materials. He must demolish all fixed installations such as foundations, concrete or metal supports, etc. demolish concrete areas, decontaminate decontaminate the soil if this has been done, or generally return the site to as close to its original state as possible. to its original state. He may not abandon any equipment or materials on the site or in the surroundings. For the storage of demolition materials, the Contractor must obtain the approval of the site from the contract engineer. The materials must be covered with a layer of earth, and the site must be adequately drained to prevent erosion.

Once the equipment has been removed, a report drawn up under the responsibility of the inspection team will record the restoration of the site. It must be drawn up and attached to the works acceptance report.

Payment of the fixed price for the removal of the equipment can only be made on the basis of this report recording the restoration of the site, including the quarries used.

## Treatment and waste management

During the works, the Contractor will ensure that the entire site and its surroundings are kept clean and that the waste produced is properly managed by taking the following measures the following measures:

- Following appropriate procedures for the storage, collection, transport and disposal of hazardous waste. disposal of hazardous waste. For waste such as used oil, it is essential to For waste such as used oil, it is essential to collect it and pass it on to approved collectors;

- Clearly identify and demarcate disposal areas and specify which materials may be deposited in each area;

- Control the placement of all construction waste (including soil excavations) approved disposal sites (>300 m from rivers, streams, lakes or wetlands) marshland);

- Place all rubbish, metals, used oils and excess materials produced during construction in authorised areas, incorporating recycling systems and separation of materials;

- The Contractor will take the necessary steps to avoid dispersion by wind or rainwater, for example, before disposing of the waste;

- The products of stripping the earthworks right-of-way will be deposited and possibly reused,

- Soil from the right-of-way will be transported to the areas to be backfilled or disposed of at public landfill sites;

- Minimising the generation of waste during construction and reusing construction waste wherever possible;

The following measures must be taken for site maintenance:

- Identify and mark out areas for maintenance equipment (away from rivers, streams, lakes or marshland) or marshy land) ;

- Ensure that all maintenance equipment activities are carried out in demarcated maintenance areas. maintenance areas;

- Never dispose of oil or pour it on the ground, in watercourses, low-lying areas, cavities in disused quarries, etc. cavities in disused quarries

## Preventive measures against noise pollution and dust emissions

The Contractor will pay particular attention to limiting any noise pollution. To this end, he must comply with the noise thresholds prescribed by law.

He will take care to limit the use of noisy machines to what is strictly necessary and will stop those that are not being used (generator set for example). Except in emergencies, noise pollution (machinery, vehicles, etc.) in the vicinity of dwellings will be prohibited from 7 p.m. to 8 a.m. as well as at weekends and on public holidays.

During the execution of the work, to combat dust and inconvenience, the contractor must:

- limit the speed of construction-related traffic to 24 km/h in the streets within a radius of 200 metres around the site and limit the speed of all vehicles on the site to 16 km/h.

## Storage and use of potentially polluting substances

As a general rule, the storage and handling of potentially polluting or dangerous substances (oils, fuel, etc.) must comply with the following principles:

- limiting the quantities stored ;

- organised storage, on a site or in a way that does not allow access by anyone outside the worksite ;

- handling by responsible personnel;

- the storage site must be marked with a sign indicating the nature of the danger.

- Liquid chemicals will be stored in retention tanks to prevent accidental spills and soil pollution. and soil pollution;

- The chemicals used must have a safety data sheet (SDS) to be to be displayed at the storage location

## Fuels and lubricants

If the contractor uses fuels and lubricants on the site, they must be stored in watertight containers placed on level, clean and stable ground. The containers will be isolated from the ground by a plastic sheeting or absorbent material (sand or sawdust) to allow any accidental spills to be recovered. accidental spillage. At the end of the works, the site will be cleared of all traces or by-products.

## Other potentially polluting substances

The use of other potentially polluting substances will be reported to the Engineer prior to their use.

The company will provide proof of the legal nature of their use and the Engineer will notify the competent technical services for authorization and, if necessary, prescribe precautionary measures. Technical services for authorization and, if necessary, precautionary instructions.

## Management of accidental pollution

In the event of accidental pollution, the Contractor will notify the Engineer without delay. Depending on the component of the environment affected by the pollution, the competent technical services will be notified. The Contractor will take all necessary steps to put an end to the cause of the problem and to treat the pollution. The prescribed precautionary measures must be implemented rapidly.

## Response to accidental pollution

In the event of an accidental spill of polluting substances, the following measures must be taken:

- avoid soil contamination by sprinkling specific absorbent products ;

- if the site is close to a water source (well, stream, etc.), prevent contamination of the water by first blocking, damming or earth bunding the area;

- Excavate polluted soil in line with the infiltration surface;

- treat polluted areas in an environmentally sound manner (landfill, burial, incineration, etc.), incineration, depending on the nature of the pollution).

## Protection of natural areas against fire

The regulations in force (Forestry Code) will be strictly applied. In general the use of fire is forbidden on the worksite unless expressly authorised by the Engineer within the limits the permissions granted by the national regulations in force. In this case, the Contractor observe the following minimum instructions:

- burning authorised only in light winds ;

- the site must be cleared of undergrowth to a radius of twenty metres;

- fire under the constant supervision of a competent person armed with fire-fighting fire-fighting equipment;

- if the fire spreads, the emergency services and the project manager must be alerted rapidly by any means ;

- the fire must be completely extinguished at the end of the burn. Covering with earth is prohibited.

## Preserving the landscape integrity of the site

No damage will be done to the vegetation outside the right-of-way of the structures, access points or planned work or storage areas. In addition, protective measures for protected or rare species should be taken. or rare species.

Only felling of trees authorised by the forestry service will be tolerated (comply with the provisions of the code for tree felling or deforestation). Penalties are incurred in the event of unauthorised felling of trees or destruction of site vegetation. The Contractor should carry out compensatory planting after the works in the event of deforestation or tree felling.

The materials used for the work (sand and gravel in particular) must come from quarries and sand pits authorised and controlled by the Mining Department. In accordance with the provisions of the Mining Code, quarries and borrow pits must be rehabilitated.

In the event of significant changes to the site, the site may be required to be restored before the site is withdrawn. of the site.

Any environmentally sensitive areas must be avoided by the project (e.g. seasonal flood zones). seasonal flooding). In addition, every precaution must be taken to preserve water sources (wells, springs, etc.). water sources (wells, springs, fountains, ponds, etc.).

## Social and cultural aspects

To enable the project to generate positive spin-offs for the host social environment, the Contractor will ensure that :

1. prevent the project from altering historical, archaeological or cultural sites ;

2. take into account the concerns of women and encourage their involvement in decision-making decision-making ;

3. give priority to recruiting unskilled labour from the local population.

The following measures should be taken in the event that objects of cultural or religious value are uncovered during excavations excavations:

- stop work immediately following the discovery of any material of possible archaeological, historical or palaeo archaeological, historical or palaeontological value, or other cultural value, to inform the find to the developer and notify the relevant authorities;

- protect the objects as far as possible using plastic covers and, where necessary, take steps to If necessary, take steps to stabilise the area in order to protect the objects properly;

- resume work only after receiving authorisation from the relevant authorities.

## Safety of people and property

- ensuring traffic safety.

- If necessary, the trenches will be surrounded by solid barriers,

- the barriers and footbridges will be illuminated at night,

- provide the required signage and guarding.

- vehicles must be able to pass through, unless absolutely impossible

- roads will not be cut at the same time over more than half their width

- trenches running alongside roads and involving the road right-of-way must not be open for more than more than 200 m in length;

- the walls of local residents and public road structures, such as kerbs, bollards, etc., must not be damaged in any way such as kerbs, bollards, etc.; electricity or telephone lines and pipes and cables of any kind of any kind encountered in the ground.

- Maintain in working order, throughout the duration of the works, the existing cables and existing pipes and installations for the distribution of drinking water or the evacuation of waste water.

## Abandonment of installations at the end of the works

At the end of the work, the Contractor must carry out all the work required to restore the site to its original state.

The Contractor shall recover all his equipment, machinery and materials. He may not abandon any equipment or materials on the site or in the surrounding area. The concrete areas are demolished and the demolition materials demolished and the demolition materials deposited on a suitable site approved by the engineer. At the time of withdrawal, the drains of the to prevent accelerated erosion of the site.

If it is in the interest of the Owner to recover the fixed installations for future use, the Administration may ask the Contractor to hand over, without compensation, any installations subject to demolition during a withdrawal.

Once the equipment has been removed, a report recording the restoration of the site must be drawn up and attached to to the official acceptance report

SCHEDULE UNIT PRICE

| N° | DESCRIPTION | UNIT | Unit Price in figures | Unit Price in Words |
| --- | --- | --- | --- | --- |
| I | PRELIMINARY WORKS |  |  |  |
| 100 | Installation of site with supply and removal of equipment | Ls |  |  |
| 101 | Transportation of materials | Ls |  |  |
|  | SUB TOTAL I |  |  |  |
|  | Rehabilitation of boreholes |  |  |  |
| II | FORAGE |  |  |  |
| 201 | Drilling works and borehole development and pumping test | H |  |  |
| 202 | Physico-chemical, bacteriological analysis and water treatment with chlorine | Ls |  |  |
|  | SUB TOTAL II |  |  |  |
| III | SUPPLY AND INSTALLATION OF PUMP |  |  |  |
| 300 | Purchase and installation of Electric pump with the following characteristics: Q: 4.2 m3/h, HMT: 100-120 m, P= 1.6kw mark: Grundfos and an electrical control box with CU200 float input, including S & I of a control box in a control room (constructed) + Installation of automatic control system | U |  |  |
| 301 | Supply and installation of drainage piping (discharge pipe diameter 40) plus connection accessories (safety rope, safety collar, blue cable or flat cable 3*2.5mm2 or 4*2.5mm2 and all other suggestions) | Ls |  |  |
| 302 | Electrical connections and accessories | Ls |  |  |
|  | SUB TOTAL III |  |  |  |
|  | Construction of catchment |  |  |  |
| 500 | Construction of catchment 1.5x1.5x60 (excavation/Stripping of the ground for the base of the collection chamber and supply and installation of 10cm thick stabilized sand bed under a clean slab. Reinforced concrete at 350kg/m3 of cement for the collection chamber equipped with two openings and closing slabs and all required accessories and 115mm thick brick masonry around pit 1.5 x 1.5 x 0.6m using approved quality blocks, including plastering) | LS |  |  |
| 501 | Provision and extension of water pipeline from catchment to community and installation of pipes and S&I of soft sand, netting and pipe indicator, including one stand tap with two heads | LM |  |  |
|  | SUB TOTAL V |  |  |  |

## BILL OF QUANTITIES AND ESTIMATES

| N° | DESCRIPTION | UNIT | QTY | U.PRICE | T.PRICE |
| --- | --- | --- | --- | --- | --- |
| I | PRELIMINARY WORKS |  |  |  |  |
| 100 | Installation of site with supply and removal of equipment | Ls | 1 |  |  |
| 101 | Transportation of materials | Ls | 1 |  |  |
|  | SUB TOTAL I |  |  |  |  |
|  | Rehabilitation of boreholes |  |  |  |  |
| II | FORAGE |  |  |  |  |
| 201 | Drilling works and borehole development and pumping test | H | 3 |  |  |
| 202 | Physico-chemical, bacteriological analysis and water treatment with chlorine | Ls | 3 |  |  |
|  | SUB TOTAL II |  |  |  |  |
| III | SUPPLY AND INSTALLATION OF PUMP |  |  |  |  |
| 300 | Purchase and installation of Electric pump with the following characteristics: Q: 4.2 m3/h, HMT: 100-120 m, P= 1.6kw mark: Grundfos and an electrical control box with CU200 float input, including S & I of a control box in a control room (constructed) + Installation of automatic control system | U | 3 |  |  |
| 301 | Supply and installation of drainage piping (discharge pipe diameter 40) plus connection accessories (safety rope, safety collar, blue cable or flat cable 3*2.5mm2 or 4*2.5mm2 and all other suggestions) | Ls | 3 |  |  |
| 302 | Electrical connections and accessories | Ls | 3 |  |  |
|  | SUB TOTAL III |  |  |  |  |
|  | Construction of catchment |  |  |  |  |
| 500 | Construction of catchment 1.5x1.5x60 (excavation/Stripping of the ground for the base of the collection chamber and supply and installation of 10cm thick stabilized sand bed under a clean slab. Reinforced concrete at 350kg/m3 of cement for the collection chamber equipped with two openings and closing slabs and all required accessories and 115mm thick brick masonry around pit 1.5 x 1.5 x 0.6m using approved quality blocks, including plastering) | LS | 1 |  |  |
| 501 | Provision and extension of water pipeline from catchment to community and installation of pipes and S&I of soft sand, netting and pipe indicator, including one stand tap with two heads | LM | 500 |  |  |
|  | SUB TOTAL V |  |  |  |  |
|  | SUMMARY |  |  |  |  |
|  | I. PRELIMINARY WORKS |  |  |  |  |
|  | II. FORAGE |  |  |  |  |
|  | III. SUPPLY AND INSTALLATION OF PITCHING MEANS |  |  |  |  |
|  | V. CONDUIT PIPING |  |  |  |  |
|  | AMOUNT HT TAXABLE |  |  |  |  |
|  | VAT 19.25% |  |  |  |  |
|  | AMOUNT WITH ALL TAXES INCLUDED (TTC) |  |  |  |  |
|  | AIR (2,2 or 5.5%) |  |  |  |  |
|  | NET PAYABLE |  |  |  |  |
|  | The Present bill of quantities and cost estimate is closed at the sum of (TTC): ………………………………………………………………………………… francs CFA |  |  |  |  |

##### GENERAL REMARKS

###### Schedule of prices and detailed estimates

- The Schedule of prices must be taken into account by the bidder strictly with the General Regulations of the invitation to tender, the General and Special Administrative Conditions and the Technical Specifications and the plans.

- The quantities specified in the Bill of Quantities and Estimates are estimated quantities and provisional. They shall be a common base for the evaluation of offers and the award of the contract. The base of regulations shall be the real quantities of ordered and executed works such as measured by the contractor and verified by the Project Manager and evaluated at the rate and price specified in figures in the Schedule of prices presented by the contractor in his/her offer.

- Except otherwise stated in the contract, the prices offered by the contractor in the Schedule of prices in figures included in his/her offer must include all the construction installations, labour, supervision, building materials, mounting, maintenance, insurance, overheads and profits, taxes, duties and dues as well as coverage for general risks, commitments and other obligations implicitly specified in contract.

- A price must be indicated for each item in the bill of quantities and estimates in figures, whether the quantities are specified or not. The cost of items for which the contractor did not indicate a price shall be considered as being covered in the bill of quantities and estimates in figures.

- The complete cost in accordance with the provisions of the contract should be included in the items specified in the Schedule of prices and the Bill of Quantities and Estimates in figures. Where an item is not specified, the corresponding cost shall be considered as having been distributed among the other prices mentioned.

- The general indications and the description of works and building materials are not necessarily repeated or summarized in the Schedule of prices and the Bill of Quantities and Estimates included in the Tender File. The references, explicit or implicit, to the appropriate sections of the file must be considered before giving a figure to the prices for each item of the Schedule of prices and bill of quantities and estimates in figures submitted in the offer.

- During the evaluation of offers, possible arithmetical errors noticed in the Schedule of prices and the Bill of Quantities and Estimates will be corrected according to the provisions of article 28 of the General Regulations of the invitation to tender.

- The method used to establish executed services in view of the regulations must be in accordance with the norms and directives  mentioned  in  the  Special  Technical  Conditions  of  the  invitation  to  tender

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

# TENDER FILE

##### CONTRACTING AUTHORITY:

THE MAYOR OF LIMBE III COUNCIL

##### TENDER BOARD:

LIMBE III COUNCIL INTERNAL TENDERS BOARD

OPEN NATIONAL INVITATION TO TENDER

No. 009/ONIT/LIIIC/L3C.TB/2026 OF 04/03/2026

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

#### FINANCING: PIB 2026 MINEE. RECORD NO:

Annex No. 1: Model tender

Document No. 8:

MODEL FORMS

###### ANNEX No. 1: MODEL TENDER

I the undersigned Mr. …………………………………… Taxpayer n° ………………………………….

Acting on the name and on behalf of ………………. P.O. BOX ………..

###### After having taken knowledge, of all relative files of the present contract document for the FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY Submit and commit to execute the works in accordance with the invitation to tender file according to the prices that I have fixed after having appreciated to my point of view and under my responsibility, the nature and the benefit, which make up the sum of	Francs cfa all taxes included.

Amount in figures FCFA TTC: ………………………..

  - - Commit to undertake from the receipt of the service order to begin works given out by the Contracting Authority, the setting up of the personnel for the works and the material as foreseen in the terms of the contract file.

  - - Declare that this tender remains valid within ninety (90) days counting from the limit date of the submission of the bid.

  - - Commit to respect the delays of three (03) months foreseen by the planning of execution of the works that I myself have established.

  - - Affirm by right at the risk of termination that I have not fallen as well as the enterprise for which I act, under the influence of legal interdictions decreed in the Republic of Cameroon.

Done at…………… on…………………

Signature (s)

###### ANNEX No. 2: MODEL BID BOND

Bank ……………………………………………………. Reference of guarantee: No. ……………………………. To; the Mayor of LIMBE III COUNCIL

Republic of Cameroon

Invitation to Tender No ……………….

###### BID BOND FOR THE EXECUTION OF THE FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY, the Contractor(5) ……………………………………….hereby submits on ……………………. to the Mayor of Limbe III Council a bid relating to THE FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

To this effect, and in keeping with the conditions stated in the Tender file, the bidder shall present to The Mayor of the LIMBE III COUNCIL acting in the capacity of Contracting Authority, a bid bond amounting to CFA Francs

……………………………………………………….…………… (6).

By this guarantee, we the undersigned,(7)………………………………….with our registered office in	,

are committed towards The Mayor  of the LIMBE III COUNCIL, through the bidder for the sum of CFA Francs

………………………(in figures)……………………………………………..

…	( in full).

By this guarantee, we irrevocably commit ourselves, without any argument or delay, to pay into an account indicated by The Mayor  of the LIMBE III COUNCIL, the amount of the guarantee at the first written request, as soon as the latter shall inform us in writing that the bidder does not keep the commitment he took in his tender.

The request for payment of guarantee shall be countersigned by The Mayor of the LIMBE III COUNCIL. This guarantee shall be released latest thirty (30) days after the expiration of the validity of the tender or, in case the enterprise shall be the successful bidder, after presentation of the performance bond which shall be kept by the Regional Tenders Board .

The laws as well as the jurisdiction of application for the guarantee shall be those of the Republic of Cameroon. Done at ……………………….., on ……………………..

Mr (Mrs)……………………………….

Signature(s) & stamps ……..

- Bidder

- Stated in the Special regulations governing the invitation to tender

- Bank

###### ANNEX No. 3: MODEL OF PERFORMANCE BOND (RETENTION FUND)

Bank:

Reference of bank guarantee: N°………………………………………………………………………

To the Mayor of LIMBE III COUNCIL

###### (Contracting Authority)

The enterprise ………………………………………………………………………

SECURITY BOND FOR THE GUARANTEE OF GOOD EXECUTION OF WORKS FOR THE FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY We, Bank…………………………………………………………… have been informed that between the Mayor of Limbe III Council acting as the Contracting Authority, and acting as entrepreneur, a contract

###### has been concluded FOR THE FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY covering the guarantees, engagement and other liabilities being incumbent upon the entrepreneur because of the contract of an amount equal to…………………………

We, Bank	engage ourselves irrevocably and without profit of discussions by this present, to

pay in favour of the Cameroonian administration at the first written request of the Regional Delegate of Public Contracts for the South West and within eight (08) weeks maximum period, up to the amount of this present guarantee, the sum of

………………………………………………………………..

All that could be due the Contracting Authority by the entrepreneur because the entrepreneur would not fulfil one or several of his/her engagement as stipulated in his/her bid.

A mobilisation request of this present guarantee will be object of a justifying recommended letter with accused receipt and copy to the entrepreneur clearly formulating completely the reasons of this request.

This present banking guarantee will enter in force at the date of notification of the contract to the entrepreneur. The original of this present guarantee will be preserved in the services of The Mayor Limbe III Council. This guarantee will be released within sixty (60) days counting from the date of the provisional reception of works. After this date, the guarantee will be without object and should be returned to us without express demand of our part. The law as well as the jurisdiction applicable to this guarantee are those of the Republic of Cameroon.

Done at…………… on…………………

Signature (s)

###### ANNEX No. 4: THE MODEL DECLARATION TO TENDER

Name of project:…………………………..Invitation to tender No. :………………… Construction of ………………………

I (We) the undersigned (8) ……………………………………………………………..

Acting in the capacity of (9) ……………in the name and on behalf of (10)	at

…………………….RC No. …………………by virtue of the power vested in me (us), domiciled at P.O. Box	(Town)

………………, telephone N°	, after having studied all the documents of the tender file relating to the

Invitation to Tender N°	, and after having assessed in my (our) point of view and under my (our)

responsibility the nature and difficulties entailed with the execution of the contract, I (we) do hereby tender and commit myself (ourselves) to carry out works FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY - LIMBE III MUNICIPALITY in keeping with the terms and conditions of the tender file.

I commit myself (We commit ourselves) in case my (our) tender is retained, to execute the contract within ……………… (	)months as from the date of notification of award of the contract.

I hereby commit myself (We hereby commit ourselves) to maintain the amount of my (our) tender for a period of sixty (60) days with effect from the dateline for submission of bids.

Done at ……………………………. , on ………………

General Manager

Signature(s)…………………….

Bidder(s)…………………………………. For companies, indicate:

The company (company or trade name, form, nationality and registered office)

« represented by the undersigned	» (name, first name and status)

For companies without a legal status, indicate:

« We, the undersigned,	»

(For each person: name, first name, company name, nationality, location of the registered office)

« Constituted in a group of companies for the execution of this Jobbing Order, jointly commit ourselves	»

- Name, first name, profession, residence

- Position in the enterprise

- Company name

###### ANNEX No. 5: MODEL OF START-OFF ADVANCE BOND

Bank …………………………………………………. Reference of guarantee No.……………………………

###### To the Mayor of LIMBE III COUNCIL Republic of Cameroon

Invitation to Tender No. ……………….

BANK GUARANTEE FOR THE REFUND OF THE START-OFF ADVANCE RELATING FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY - LIMBE III MUNICIPALITY. We…(Bank) have been informed that a contract shall be signed between The Mayor  for the

LIMBE III COUNCIL, acting in the capacity of Contracting Authority, and	, acting as contractor FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY -LIMBE III MUNICIPALITY. In compliance with the provisions of Article	of

Contract N°	, the contractor shall be bound to present to the Public independent conciliator LIMBE III COUNCIL, Contracting

Authority, a bank guarantee with the purpose to assure the refund of the start-off advance granted to the enterprise and amounting to CFA Francs ……………………………………… ………………………………………...

We, …………………………………..(bank) do hereby commit ourselves, irrevocably and without arguing to pay to The Mayor  of the LIMBE III COUNCIL, at the written request of The Mayor  of the LIMBE III COUNCIL, and within THREE (03) weeks the amount of this guarantee, that is to say. …………….……………………. , all the amounts that the contractor may owe the Contracting Authority for failing to fulfil one or more of his obligations under the contract.

The request to partially or fully stake this guarantee shall be the subject of a registered letter of justification with confirmation of receipt and a copy to the contractor clearly stating and supplementing the reasons for his request. This letter shall be countersigned by The Mayor of the LIMBE III COUNCIL.

The bank guarantee shall take effect as from the date of payment of the start-off advance. The original of this guarantee shall be kept by the Regional Tenders Board. The guarantee shall be released upon refund of the full amount of the advance. After this date, the guarantee shall no longer apply and shall be returned to us without express request.

The laws as well as the jurisdiction of application for the guarantee shall be those of the Republic of Cameroon. Done at ……………………….., on ……………………..

Mr (Messrs)……………………………………….. Signature(s) & stamps of the bank

ANNEX No. 6: SUB-UNIT PRICE DETAIL

| Designation of Works : |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| N° price | Daily output |  | Total Quantity |  | Duration (days) |
|  | / day |  |  |  |  |
| WORKMANSHIP | Category | Number | Daily Salary | Days paid | Amount |
|  | Site engineer |  |  |  |  |
|  | Site foreman |  |  |  |  |
|  | Team chiefs |  |  |  |  |
|  | Administrative staff |  |  |  |  |
|  | Driver |  |  |  |  |
|  | Specialised Technicians |  |  |  |  |
|  | Labourers |  |  |  |  |
|  | Store keeper |  |  |  |  |
|  | Total A |  |  |  |  |
| MACHINES OR EQUIPMENT |  |  |  |  |  |
|  | Type | Quantity | Daily rate | Days paid | Amount |
|  | Pickup for follow-up |  |  |  |  |
|  | Small equipment |  |  |  |  |
|  | Total B |  |  |  |  |
| DIVERSES MATERIALS |  |  |  |  |  |
|  | Type | Quantity | Unit Price | Consumption | Amount |
|  | * |  |  |  |  |
|  | * |  |  |  |  |
|  | * |  |  |  |  |
|  | Total C |  |  |  |  |
| D | TOTAL DRY PRICE A+B+C |  |  |  |  |
| E | General site expenses |  | X% | D x X% |  |
| F | General head office expenses |  | Y% | D x Y% |  |
| G | TOTALCOST PRICE |  |  | D + E + F |  |
| H | Risks + benefits |  | Z% | G x Z% |  |
| P | TOTAL COST PRICE WITHOUT TAXES |  |  | G + H |  |
| V | SELLING UNIT PRICE WITHOUT TAXES |  |  | P/QTE |  |

ANNEX No. 7:

##### MODEL OF COMMITMENT OF AVAILABILITY

To Whom It May Concern:

Subject:  COMMITMENT OF AVAILBILITY.

I the undersigned, (specify Name, qualification -diploma or certificate) is committed and will be available to work as (specify post occupied) with (name of enterprise) if Open National Invitation to Tenders N° 009/ONIT/LIIIC/FAKO/L3C.TB/PIB2026 OF 04/03/2026 FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY.

###### awarded to ……………………………………..

Done at 	the

Sign;

##### ANNEX NO: 8

SITE VISIT REPORT [not more than five (05) pages]

- INTRODUCTION

TENDER Nº (with project title) ………………………………………………………………… NAME OF ENTERPRISE …………………………………………………………………….. DATE: ……………………………………………… TIME: ……………………………………….

- COMMENTARY:

II-1) Nature of the project site …………………………………………………….

II-2) Accessibility to the project site: …………………………………………………… II-3) Vegetation (trees, shrubs etc) ………………………………………………………

II-4) Topography of the site ……………………..

- AVAILABILITY OF SERVICES (water, electricity, etc)

- AVAILABILITY OF CONSTRUCTIONAL MATERIAL (stones, sand, gravel, wood etc)

- DIFFICULTIES: ………………………….……………………………………………….

…………………………………………………………………………………………………………………….……………………

……………………………………………………………………………………………….

V) CONCLUSION …………………………………………………………………………

……………………………….…………………………………………………………………………………………………………

………….

SIGNATURES:

Contractor’s Engineer

`

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

# TENDER FILE

##### DELEGATED CONTRACTING AUTHORITY:

THE MAYOR OF LIMBE III COUNCIL

##### TENDER BOARD:

LIMBE III COUNCIL INTERNAL TENDERS BOARD

OPEN NATIONAL INVITATION TO TENDER

NO 009/ONIT/LIIIC/FAKO/L3C.TB/PIB2026 OF 04/03/2026/

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY

Peace        Development

Paix    Développement

L. III C (BIMBIA)

REPUBLIC OF CAMEROON

PEACE-WORK-FATHERLAND

--------------------

SOUTH-WEST – REGION

--------------------

FAKO DIVISION

--------------------

LIMBE III SUB DIVISION

--------------------

LIMBE III COUNCIL

--------------------

Po Box; 97 Limbe; Tel 33030536. Fax 3333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

REPUBLIQUE DU CAMEROUN

PAIX-TRAVAIL-PATRIE

--------------------

REGION DU SUD - OUEST

--------------------

DEPARTEMENT DU FAKO

--------------------

ARRONDISSEMENT DE LIMBE III

--------------------

COMMUNE DE LIMBE III

--------------------

BP 97 Limbe. Tel 33030536. Fax 33333133

--------------------

Email :limbe3councilbimbia@yahoo.com

www.facebook.com/limbe3council

PEACE – WORK – FATHERLAND

~~~~~~~~

SOUTH – WEST REGION

~~~~~~~~ GOVERNOR’S OFFICE

~~~~~~~~

# TENDER FILE

##### CONTRACTING AUTHORITY:

THE MAYOR OF LIMBE III COUNCIL

##### TENDER BOARD:

OPEN NATIONAL INVITATION TO TENDER

NO 009/ONIT/LIIIC/FAKO/L3C.TB/PIB2026 OF 04/03/2026  FOROFF………………….

FOR THE REHABILITATION OF THREE BOREHOLES AND A CATCHMENT WITH DISTRIBUTION LINE AT BONANGOMBE, BONABILE, CHOP FARM, MAN O’ WAR BAY.

LIMBE III COUNCI INTERNAL TENDERS BOARD

#### FINANCING: PIB 2026 MINEE. RECORD NO:

Document No. 10:

FILE OF PLANS